## All-Data
EQ_NAME | EQ_DATE | EQ_TIME | EPICNTR_LAT | EPICNTR_LONG | MAGNITUDE | FOCAL_DEPTH | FAULT_TYPE | FAULT_SOLU1 | FAULT_SOLU2 | FAULT_SOLU3 | ALT_FAULT_SOLU | MAX_MMI | EQ_COMMENT | REFERENCES | FACIL_NAME | FACIL_OWN | TYPE_FACIL | FACIL_ADD | FACIL_LAT | FACIL_LONG | EPICEN_DIST | DIST_RUPT | SITE_MMI | EST__PEAK_ACC | 0.1_SA | 0.2_SA | 0.3_SA | SM_RECORD | SOIL_TYPE | SITE_COMMENT | GRND_MOTION | DAMAGE_PAR_1 | DAMAGE_PAR_2 | RESTORATION | IMPACT_DAMAGE | EQP_STATUS | SECOND_DMG | NO_ITEMS | TYPE_EQP | CB_SUBCLAS | TR_SUBCLAS | TR_BUSHING | LA_SUBCLAS | WT_SUBCLAS | CVT_SUBCLAS | PT_SUBCLAS | CT_SUBCLAS | DS_SUBCLAS | MODS_SUBCL | DISPATCH_D | OPERATING_V | SECONDARY_V | CURRENT_RATE | BIL | CANTILEVER | MANUFACTUR | MODEL___DES | YEAR_MANUF | UWG_CLASS | WEIGHT | EQP_COMMENT | EQP_INSTAL | EQP_DAMAGE | RESTORATION | FAIL_MODE | REC_NO | REC_DATE | DAMAGE_PAR | CONTRIBUTI
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Plant | Long Beach | [5 empty] | 0.058 | 0.107 | 0.123 | 0.102 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 | [5 empty] | SF6 |  | CB |  |  |  | SF6 leaking at entrance bushing on non-CT column. Is this support column or bushing? What type of equipment. |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Plant | Long Beach | [5 empty] | 0.058 | 0.107 | 0.123 | 0.102 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2* | Circuit Breaker CB | Live Tank | [10 empty] | 230 | [7 empty] | CB |  | What type of equipment |  |  |  |  | 233 | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#2 | SCE | Transmission SS | 2nd Ave & St. Joseph | [5 empty] | 0.163 | 0.297 | 0.346 | 0.324 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  |  | Transformer TR | [11 empty] | 60 | 16 | [6 empty] | TR |  |  |  | What was problem? |  |  | 220 | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk | [5 empty] | 0.11 | 0.207 | 0.24 | 0.18 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | Cracked non-CT support column. |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk | [5 empty] | 0.11 | 0.207 | 0.24 | 0.18 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2* | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 | [7 empty] | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk | [5 empty] | 0.11 | 0.207 | 0.24 | 0.18 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | [7 empty] | TR2 | [7 empty] | 1998-10-28
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk | [5 empty] | 0.11 | 0.207 | 0.24 | 0.18 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 |  |  |  |  | General Electric | 3o D572975 |  | TR2 |  |  |  | Oil leak. Where? Which unit? |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk | [5 empty] | 0.11 | 0.207 | 0.24 | 0.18 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 | 60 |  |  |  | Pennsylvania | 3 phase |  | TR2 |  |  |  | Gas leak in man hole cover. Which unit? |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos | [5 empty] | 0.079 | 0.148 | 0.169 | 0.137 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | Blown seals on bushing #2. What is bushing #2. This is probably inner interrupter head bushing. what phases? | restored 10/5/87 @ 2300 |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos | [5 empty] | 0.079 | 0.148 | 0.169 | 0.137 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 18 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | There is also another ATB 4 or 6 |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos | [5 empty] | 0.079 | 0.148 | 0.169 | 0.137 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 9 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric |  |  | CB9 |  |  |  | This data added to reflect total of 30 at site |  |  |  | 1999-04-12
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.101 | 0.225 | 0.238 | 0.15 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA | [11 empty] | 60 | [7 empty] | LA |  |  |  | Failed porcelain. How was it mounted. |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.101 | 0.225 | 0.238 | 0.15 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Lightning Arrester LA | [11 empty] | 60 | [7 empty] | LA |  |  |  | How was it mounted. |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.101 | 0.225 | 0.238 | 0.15 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 60 | [7 empty] | TR |  | Equipment info not provided |  | Top plate gasket leaking. |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#11 | SCE | Transmission SS | Compton Blvd east of Avalon, Compton | [5 empty] | 0.094 | 0.17 | 0.188 | 0.175 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Current Trans. CT | [19 empty] | CT |  |  |  | Oil leak |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#11 | SCE | Transmission SS | Compton Blvd east of Avalon, Compton | [5 empty] | 0.094 | 0.17 | 0.188 | 0.175 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  |  | Transformer TR | [19 empty] | TR |  |  |  | Chipped bushings. Need details. |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#15 | SCE | Transmission SS | [6 empty] | 0.07 | 0.16 | 0.168 | 0.097 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | [10 empty] | 622 | 60 | [7 empty] | CB |  | Voltage and type not known |  | What was problem? |  |  |  | 1991-12-08
2-Whittier Narrows | 1987-10-04 | 3:59:00 |  |  | 5.3 | 12 | Strike-Slip | [5 empty] | SCE Report | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#33 | SCE | Transmission SS | 1371 Monterey Pass Rd | [5 empty] | 0.171 | 0.325 | 0.395 | 0.31 | No | Tertiary formation - soft rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | [11 empty] | 4 | [7 empty] | CB |  |  |  | Burnt. Is this contacts? |  |  |  | 1991-12-08
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 552 C phase | 500 |  | 3000 |  |  | General Electric | ATB-550-2 SN 0139A8759-204 | 1971 | CB15A |  | 0.2 g static seismic specification |  | Gasket leak at base of top porelain member above CT lead. | 2 days to repair. No effect on service. |  |  | 1991-11-26
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 8 | Circuit Breaker CB | Live Tank | [9 empty] | 552, 652 | 500 |  | 3000 |  |  | General Electric | ATB-550-2 | 1971 | CB15A |  | 0.2 g static seismic specification | [5 empty] | 1991-11-26
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 33 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | Oil |  | CB20A | [7 empty] | 1998-06-12
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | [11 empty] | 220 | [5 empty] | unknown |  | CB74 | [7 empty] | 1998-06-12
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | Westinghouse | ? 2 head, |  | CB74 | [7 empty] | 1991-11-26
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA |  |  |  | Free Standing | [6 empty] | Bank 11B | 500 | [6 empty] | 1972 | LA5 |  |  | Installation not verified. Associated with 500/230 kV TR Bank 11. | Failed porcelain | replaced |  |  | 1991-11-26
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 500 | [6 empty] | 1972 | LA5 |  |  | Installation not verified. Associated with 500/230 kV TR. |  |  |  |  | 1991-11-26
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Transformer TR | [10 empty] | Bank 1 | 230 | 115 |  |  |  | Westinghouse | single phase | 1953 | TR1 | [7 empty] | 1998-07-08
Coalinga | 1983-05-02 | 16:42:38 | 36.23 | 120.29 | 6.5 | 10 | [5 empty] | 8 | Data from pp9 and 21, Ref 1, Page 21 given preference MMI Map on cover of Ref 1 SM Data: CDMG 60, USGS 37 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983 | SS#12 | PG&E | [7 empty] | 0.2985 | 0.5697 | 0.664 | 0.5283 | No | (UBC S1) < 200 ft alluvium overlying sedimentary rock. |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 4 | Transformer TR | [10 empty] | Bank 11 | 500 | 230 | 374 MVA each, 1122 MVA total | 1150 (High V bushing), 900 (Low V bushing) |  | General Electric | K 546561 thru 64, auto, ccoled by OA/FA/FOA | 1972 | TR3 |  |  |  | all 500 kV bushings shifted 3/8". leaking oil | 20 days to repair. No effect on service. |  |  | 1991-11-26
Landers | 1992-06-28 | 4:57 | 34.21 | 116.43 | 7.6 | 1 | Strike-Slip | [6 empty] | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq. | SS#5 | SCE | Generating Station | Daggett | [5 empty] | 0.352 | 0.479 | 0.764 | 0.994 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra |  |  |  |  | Undamaged |  | 24 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | oil |  | CB20A | [7 empty] | 1998-04-02
Landers | 1992-06-28 | 4:57 | 34.21 | 116.43 | 7.6 | 1 | Strike-Slip | [6 empty] | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq. | SS#5 | SCE | Generating Station | Daggett | [5 empty] | 0.352 | 0.479 | 0.764 | 0.994 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra |  |  |  |  | Damaged |  | 6 | Disconnect Switch DS | [8 empty] | Low Design, Horizontal |  |  | 220 | [7 empty] | DS3 |  |  |  | out of adjustment |  |  |  | 1998-04-02
Landers | 1992-06-28 | 4:57 | 34.21 | 116.43 | 7.6 | 1 | Strike-Slip | [6 empty] | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq. | SS#5 | SCE | Generating Station | Daggett | [5 empty] | 0.352 | 0.479 | 0.764 | 0.994 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra |  |  |  |  | Undamaged |  | 48 | Disconnect Switch DS | [8 empty] | Low Design, Horizontal |  |  | 220 | [7 empty] | DS3 | [7 empty] | 1998-04-02
Landers | 1992-06-28 | 4:57 | 34.21 | 116.43 | 7.6 | 1 | Strike-Slip | [6 empty] | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq. | SS#5 | SCE | Generating Station | Daggett | [5 empty] | 0.352 | 0.479 | 0.764 | 0.994 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra |  |  |  |  | Undamaged |  | 15 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 220 | [7 empty] | LA1 | [7 empty] | 1998-04-02
Landers | 1992-06-28 | 4:57 | 34.21 | 116.43 | 7.6 | 1 | Strike-Slip | [6 empty] | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq. | SS#5 | SCE | Generating Station | Daggett | [5 empty] | 0.352 | 0.479 | 0.764 | 0.994 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Smallrad/man | [9 empty] | 220 | 13.8 |  |  |  |  | three phase, step up |  | TR2 |  |  |  | radiator leak | fixed using wrench to tighten bolts |  |  | 1998-04-02
Landers | 1992-06-28 | 4:57 | 34.21 | 116.43 | 7.6 | 1 | Strike-Slip | [6 empty] | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq. | SS#5 | SCE | Generating Station | Daggett | [5 empty] | 0.352 | 0.479 | 0.764 | 0.994 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra |  |  |  |  | Undamaged |  | 4 | Transformer TR |  | Smallrad/man | [9 empty] | 220 | 13.8 |  |  |  |  | three phase, step up |  | TR2 | [7 empty] | 1998-04-02
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 15 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  | 3000 |  |  | Westinghouse | 3200y SF15000/20000 sn2-62y1128 | 1966 | CB20 | 32000 | [6 empty] | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 24 | Circuit Breaker CB | Dead Tank | [9 empty] | 382, 222, 242, 262, 212, 312, 232, 252 | 230 | [5 empty] | Oil | 1966 | CB20A | [7 empty] | 1998-06-12
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 992 Cphase | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, flexible loop bus connection to CT | All three interrupter head support columns failed. Adjacent CT and DSW did not fail. Support structure moved from under friction clips North about 1 foot. |  |  | 51 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 822 B phase | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Center interrupter head support column failed. Entire column failed. Adjacent CT and DSW did not fail. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 722 B phase | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Interrupter head support column near disconnect switch failed. Upper part of column failed. Adjacent CT and DSW did not fail. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 822 A phase | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Interrupter head support column near disconnect switch failed. Upper part of column failed. Entire column near CT failed. Adjacent CT and DSW did not fail. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 922 A phase | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit tipped over, flexible loop bus connection to CT. | All interrupter head support columns failed. Entire column near CT failed. Adjacent CT did not fail. Adjacent DSW did fail. Support structure moved about 6" from under friction clips. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 722 A phase | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | Interrupter head support column near disconnect switch failed. The entire column failed. Adjacent CT and DSW did not fail. No significant displacement of support structure. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 822 A phase | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | All interrupter head support columns failed. The entire column failed. Adjacent CT and DSW did not fail. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Circuit Breaker CB | Live Tank | [9 empty] | 922 B & 722 C | 500 |  | 3000 |  |  | Westinghouse | SF6, Seismic, modified 1973 | 1966 | CB72s |  | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Dead Tank | [9 empty] | 292 | 230 | [5 empty] | Unknown |  | CB20 |  | it is unclear from documentation of this is a bulk oil or SF6 | [5 empty] | 1998-06-12
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Dead Tank | [9 empty] | 812 | 500 |  | 3000 |  |  | High Voltage Breaker, Inc.(Hitachi/Westinghouse) | H 550-40000-3 SN 5500A2012-203 | 1987 | CB77 | 81200 | Bushings are attached to sand ring which is bolted to CB body, 2 cycle interrupt, shake table tested | [5 empty] | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 1600 |  |  | General Electric | ATB6 y | 1967 | CB9 | [7 empty] | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 5 | Coupling Voltage Trans. CVT | [5 empty] | Structure/WT | [5 empty] | 230 | [7 empty] | CC1 | [7 empty] | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 8 | Coupling Voltage Trans. CVT | [5 empty] | CB Mounted | [5 empty] | 230 | [7 empty] | CC1 | [7 empty] | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 12 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | CC1 | [7 empty] | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 6 | Coupling Voltage Trans. CVT | [5 empty] | Structure/WT | [5 empty] | 500 | [7 empty] | CC5 | [7 empty] | 1992-01-02
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Current Trans. CT | [11 empty] | 500 | [7 empty] | CT5 |  |  | Units had flexible loops connecting CT to CB | Some of the couplings between CT and CB may have broken | required removal of contaminated ground below each leaking CT. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 6 | Current Trans. CT | [11 empty] | 500 | [7 empty] | CT5 |  |  | Units are mounted on Tit-tat-toe chair are are relatively flexible to rotation. Units had flexible loops connecting CT to CB | Oil leaks between bushing and tank. Some of the couplings between CT and CB may have broken | required removal of contaminated ground below each leaking CT. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged | Yes | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  | 821 | 500 | [7 empty] | DS1 |  |  |  | Failure of outside double post and top of inner double post. Probably due to failure of adjacent CB but taken as independent failure. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 23 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 | [7 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 5 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [7 empty] | DS2 |  |  | Bus support structure, pin and cap insulators. |  |  |  | 303 | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 30 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [7 empty] | DS2 |  |  | Ground support structure, pin and cap insulators. |  |  |  | 302 | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 8 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Bus support structure, pin and cap insulators. |  |  |  | 301 | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 12 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Ground support structure, pin and cap insulators |  |  |  | 170 | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Lightning Arrester LA |  |  |  | TR Body Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | Mounted on 500/230 kV McGraw Edison TR. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Lightning Arrester LA |  |  |  | TR Body Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | mounted on 500/230 kV Westinghouse TRs. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 7 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | Associated with 230/115 kV Pennsylvania TRs (Bank 1 &2). Mounted on long boom. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Lightning Arrester LA |  |  |  | TR Body Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | mounted on 500/230 kV General Electric TRs. One of these may have been damaged (see record 292) | One of these may have been damaged? |  |  | 151 | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 230 |  |  |  |  | Westinghouse |  |  | LA1 |  |  | Associated with W 500/230 kV TR | Porcelain failure, but unit fell to ground indicating bus connection failure. TR record 67. Not sure if this was 500 or 230 kV LA that failed. |  |  | 292 | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 500 | [7 empty] | LA5 |  | Note that the LA with the GE were composed of 4 identical sections while others had large and medium sections and a short support section. | Associated with GE 500/230 kV TRs ( at west end of site). | Unit at east end of row may have been damaged - See record 292 |  |  |  | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 500 | [7 empty] | LA5 |  | Note that the LA with the GE were composed of 4 identical sections while these had large and medium sections and a short support section. | Associated with W 500/230 kV TRs and ME TR (east end of site). | Unit at east end of row may have been damaged - See record 292 |  |  |  | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Transformer TR | [11 empty] | 230 | 115 | [6 empty] | TR1 | [7 empty] | 1998-07-17
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 7 | Transformer TR |  | Med Rad/O Manif | [9 empty] | 230 | 115 |  |  |  | Pennsylvania | Spec. 10035, sn 0-02265-5-3, | 1950 | TR1 | 211400 | Rad. elements supported from tank. C&C 94700, T&F 64400, 6970 g - 54300. | 230 LA on boom, 115 LA on rad. |  |  |  | 295 | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Large Rad/O Manif | [8 empty] | spare | 500 | 230 | 374 MVA | 1425 (High V bushing), 750 (Low V bushing) |  | Westinghouse | OA, FA, FO, Core type. | 1968 | TR3 | 606000 | Large radiators with each element supported from a TR tank. Rad. on sides and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 4 th from east end - use as spare. 230 LA on boom. 500 LA on independent latus structure. Units 1, 2 and 4 from east end of site. Welded to embedment |  | put into service when McGraw Edison units has bushing leak. |  | 68 | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Large Rad/Manif | [8 empty] | Bank 11 C phase | 500 | 230 | 374 MVA | 1425 (High V bushing), 750 (Low V bushing) |  | McGraw Edison | Spec. 13330, sn C06503-5-7, HV bushing no. 501.LL.716 | 1968 | TR3 | 490300 | Large radiators with each element supported from maniford perp. to TR tank. 70" X 127" along TR. They are supported on non-penatrating pipe at bottom and penetrating pipe at top. There are horizontal braces at bottom but not consistant (one brace was | 230 LA on rad., Welded to embedment | The 500 kV bushing shifted about 1/4" and had an oil leak at the steel/porcelain interface. Bushing was bottom attachment type rather than draw out type. Were was leak, at bushing-flange or flange -tank? | The replacement bushing is 153" from flange to top and 76" from flang down. |  | 69 | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Transformer TR |  | Large Rad/O Manif | [8 empty] | Bank 11 A & B | 500 | 230 | 374 MVA each | 1425 (High V bushing), 750 (Low V bushing) |  | Westinghouse | OA, FA, FO, Core type. | 1968 | TR3 | 606000 | Large radiators with each element supported from a TR tank. Rad. on sides and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 230 LA on boom. 500 LA on independent latus structure. Units 1, 2 and 4 from east end of site., Welded to embedment | Minor oil leaks on B phase. note that A phase (east unit) lost LA, original slides indicated minor leaks at radiators (see record 292) Operational |  |  | 67 | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 3 | Transformer TR |  | Large Rad/Manif | [8 empty] | Bank 12 | 500 | 230 | 374 MVA each | 1550 (High V bushing), 900 (Low V bushing) |  | General Electric | OA, FA, FO, sn D577035, -6, 7, HV bushing no. 11B775, LV bushing no. 11B765 | 1968 | TR3 | 600000 | 2 large radiators per side with each element supported from heavy box beam perp. to TR body and with non-penatrating connection with gusset plates for vert. load. Top connection is penetratng pipe. Each 142" long. There are diagonal braces at bottom, | West end of TR row. 230 kV LA installed on rad. | Severe oil leaks at the upper flange connection of manifold to tank. Flanges were deformed and peening was required to stop leaking. Repairs were made without the need to removed radiators or manifold. | Units were out for several days? Extensive excavation to removal contaminated soil. |  |  | 1991-12-22
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  | Wave trap size is about 4 feet in diameter and 6 feet long | mounted on support with CVT |  |  |  |  | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  | Wave trap size is about 2 feet in diameter and 4 feet long | mounted on support with CVT |  |  |  |  | 1991-12-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#24 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.2867 | 0.3669 | 0.4472 | No | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 6 | Wave Trap WT |  |  |  |  | H. Post-Insulator Mount | [6 empty] | 500 | [7 empty] | WT2 |  |  | mounted on support with CVT |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 21 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | Oil |  | CB20A | [7 empty] | 1998-06-12
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | 3 o Dead Tank | [10 empty] | 230 |  |  |  |  | BBC | 242PA4020 |  | CB78 |  | A relatively new three phase CB was undamaged. | Welded anchorage into embedment |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Circuit Breaker CB | 3 o Dead Tank | [10 empty] | 115 |  |  |  |  | BBC |  |  | CB |  | A relatively new three phase CB was undamaged. | Welded anchorage into embedment |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Hitachi | HVB242-400001 |  | CB20 |  | These were associated with Capacitor banks. | These were located on a new site adjacent to and north of the 230 kV site. |  |  |  | 153 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Coupling Voltage Trans. CVT | [5 empty] | Structure/WT | [5 empty] | 230 | [7 empty] | CC1 |  |  | Mounted on 2 legged lattice structure with WT | Porcelain failed at its base. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Coupling Voltage Trans. CVT | [5 empty] | Structure/WT | [5 empty] | 230 | [7 empty] | CC1 |  |  | number of power mounted and structure/wt not known. | Total number at site not known.(it is known that there were a minimum of three) |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 6 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | mounted on tall frames | Bus connections to switches were misaligned. Impact on operation is not clear but EPRI report indicates that they would not operate properly. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 117 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Bus supported. | Bus connections to switches were misaligned. Impact on operation is not clear but I seem to call that they would not operate properly. |  |  | 168 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | The LA was mounted on a long extension arm off of TR bank 4 & 4A | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | The LA was mounted on a long extension arm off of TR bank 5 | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 5 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | The LA was mounted on a long extension arm off of TR bank 4 & 4A | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Large Rad/O Manif | [9 empty] | 230 | 60 |  |  |  | Westinghouse |  |  | TR1 |  |  |  | Core damage |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Large Rad/O Manif | [9 empty] | 230 | 60 |  |  |  | McGraw Edison |  |  | TR1 |  |  | this was spare. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 2 | Transformer TR |  | Large Rad/O Manif | [9 empty] | 230 | 60 |  |  |  | Westinghouse |  |  | TR1 |  |  | Station power components were mounted on "pipe" framed structure. This may have contributed to bushing and LA damage. There was not much slack between porcelain and support structure. | Damage to tertiary 12 kV bushings to station power, | After replacement there was still problems. Lightning Arrester had to be removed. It is not clear if this impacted station operations or operation of TRs. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 6 | Transformer TR |  | Large Rad/O Manif | [9 empty] | 230 | 115 |  |  |  | Westinghouse |  |  | TR1 |  |  |  | Damaged LA swung and chip shed on bushng or LA | After replacement there was still problems. Lightning Arrester had to be removed. It is not clear if this impacted station operations or operation of TRs. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Wave Trap WT |  |  |  |  | frame mounted | [6 empty] | 230 | [7 empty] | WT1 |  |  | Mounted on support with CCVT | It is unknown how many there are. There are at least three. |  |  |  | 1998-07-20
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS | SS#25 | PG&E | Transmission SS | [6 empty] | 0.2366 | 0.3513 | 0.466 | 0.5807 | No | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 3 | Bus Support | [11 empty] | 230 | [7 empty] | BS |  | Transfer busses above TR banks | Transfer busses were support at top of bus support structure. Transfer busses were supported by pin and cap post insulators. | On each of two structures, post insulators failed. In one case it dropped the bus across flexible bus connected to the bus support structure. In one case a bell on a bus string was damaged and was replaced. |  |  | 93 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 34 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [7 empty] | CB20A |  | Bulk oil type CB. | [5 empty] | 1998-07-20
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged | Yes | 2 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [7 empty] | CB20A |  | Bulk oil type CB. |  | Sheds on bushing chipped due to failure of switch above CB. |  |  | 123 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 522A | 500 |  |  |  |  | Westinghouse | SF6, Seismically Strengthened 1973 |  | CB72s |  |  | Units anchored with unwelded, single bolt friction clips. Rigid link between CB and CT. l | Failure of one support column next to CT. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 722A | 500 |  |  |  |  | Westinghouse | SF6, Seismically Strengthened 1973 |  | CB72s |  |  | Units anchored with unwelded, single bolt friction clips. Rigid link between CB and CT. | Failure of one support column next to DS. |  |  | 147 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 10 | Circuit Breaker CB | Live Tank | [9 empty] | 722, 622, 522, 512 | 500 |  |  |  |  | Westinghouse | SF6, Seismically Strengthened 1973 |  | CB72s |  |  | Units anchored with unwelded, single bolt friction clips. Nine of the 12 units had flexible links between CB and CT, three had rigid links (522). | One phase toppled from slab, others moved, did not move or did not move significantly. Details of damage to specific units were difficult to determine from pictures. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Dead Tank | [9 empty] | 612 | 500 |  | 3000 |  |  | High Voltage Breaker, Inc. | HVB-550-400000-0, sn550A2009-205 |  | CB77 | 81200 | Bushing has flange bolted to CB body. | Units anchored with about a foot of weld (only one side could be seen in picture) to a cast in place embedment. |  |  |  |  | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Coupling Voltage Trans. CVT | [5 empty] | Structure/WT | [5 empty] | 230 | [7 empty] | CC1 | [7 empty] | 1992-01-02
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 500 | [7 empty] | CC5 |  |  | These were adjacent to dead-tank CB. |  |  |  |  | 1992-01-02
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 6 | Coupling Voltage Trans. CVT | [5 empty] | Structure/WT | [5 empty] | 500 | [7 empty] | CC5 |  |  | Mounted on lattice structure with WT. Two may not have had WTs. Units after they were repaired or replaced: 5 GE with 3 porcelain segments and 1 (WE?) with 4 porcelain segments. |  |  |  |  | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Current Trans. CT | [10 empty] | 522A | 500 | [7 empty] | CT5 |  |  | Units had flexible connects to CB. Units held with friction clips. Support structure very flexible. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 3 | Current Trans. CT | [10 empty] | 622A & B | 500 | [7 empty] | CT5 |  |  | Units had rigid connects to CB. Units held with friction clips. Support structure very flexible. | Porcelain failed near top. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 7 | Current Trans. CT | [11 empty] | 500 | [7 empty] | CT5 |  |  | Units had flexible connects to CB. Units held with friction clips. Support structure very flexible. | Ceramic failed near top in most cases. In one case it failed about middle. One unit toppled from pad. Some failures may be due to secondary damage when CB failed. Bus connections to CB on several units fail at CB side, presumably after porcelain fai |  |  | 108 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 |  |  |  | damage unkown |  |  |  | 1998-07-20
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 |  |  |  | Just the post insulator on the contact side failed. It was connected to the bus that fell. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 |  |  |  | unit adjacent to the dead tank CB had the blade misaligned. It is not know if it was functional. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 2 | Disconnect Switch DS | [8 empty] | Vertical Swing |  | 775 | 500 |  |  |  |  | Southern States |  |  | DS1 |  |  |  | The insulator on the contact side had bolts fail at base of post. Inadequate thread penetration. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 5 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 |  |  |  | One or both of the post insulators on the hinge side failed and the post insulator in the contact side also failed. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 7 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 |  |  |  | One or both of the post insulators on the hinge side failed and the post insulator in the contact side did not fail. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 8 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 |  |  |  | One or both of the post insulators on the hinge side failed and the post insulator in the contact side did not fail. |  |  | 112 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 17 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 | [7 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [7 empty] | DS2 |  |  | Bus supported. |  |  |  | 102 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [7 empty] | DS2 |  |  | Bus supported. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged | yes | 12 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [7 empty] | DS2 |  |  | Bus supported, bus sectioning switch. | It appears these DS were pulled apart by the out of phase dynamic response of adjacent bus sections |  |  | 121 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [7 empty] | DS2 |  |  | Bus supported , bus sectioning switch. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Bus supported. |  |  |  | 119 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Bus supported. |  |  |  | 120 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 114 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Supported on its own structure. | Not sure if any of these were damaged. |  |  | 150 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | Mounted on radiator of 500/230 kV TR, Bank 9. |  |  |  |  | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | Mounted on 230/115 kV Bank 8. It is mounted on radiator. |  |  |  | 101 | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 500 | [7 empty] | LA5 |  |  | Lattice-type post support. Adjacent to 500/230 kV TR, Bank 9. |  |  |  | 100 | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Transformer TR | [10 empty] | Bank 1C | 230 | 115 |  |  |  | General Electric |  | 1989 | TR1 | [7 empty] | 1998-07-17
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 8 | Transformer TR | [10 empty] | Bank 1, 2, 3 | 230 | 115 |  |  |  | General Electric |  | 1950 | TR1 | [7 empty] | 1998-07-17
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Transformer TR |  | Small Rad | [8 empty] | Bank 8 | 230 | 115 |  |  |  | McGraw Edison | OA, FOA, FOA, sn C04169-5-2 | 1972 | TR1 | 285000 | 11270 g of oil with wt of 84500, rad stick out 66", have large rad supports and relatively small rad. There is tertiary 13200 winding. Each TR has 5 bushings. Tertiary bus looks very flexible and there is little slack to bushings and LA. Note TR for | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts. |  | 293 | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Small Rad | [9 empty] | 230 | 115 |  |  |  | McGraw Edison | OA, FOA, FOA, sn C04169-5-2 | 1972 | TR1 | 285000 | 11270 g of oil with wt of 84500, rad stick out 66", have large rad supports and relatively small rad. There is tertiary 13200 winding. Each TR has 5 bushings. Tertiary bus looks very flexible and there is little slack to bushings and LA. Note TR for | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts. |  | 293 | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Transformer TR |  | Large Rad/Manif | [8 empty] | Bank 9 | 500 | 230 |  |  |  | McGraw Edison | Spec. 13135-A, sn C05322--5-1 (single phase) | 1978 | TR3 | 489300 | Rad. are are mounted on 3 sides, each with large box beam perp. to TR body with 4 rad. cores on each side of beam. Over all rad. is 68" out and 138" along TR. Lower rad support is large box beam that has no diagonal bracing but there are horizontal supp | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts. |  |  | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Small Rad | [9 empty] | 500 | 12 |  |  |  | Westinghouse | FO, FA, three phase |  | TR4 | 431100 | 8020 g . TR is tall with small foot print. (about 13' x 13'). While rad are not very heavy, upper penetration supports total weight. | anchored by welding to embedment but angles are bolted to TR with what looks like small bolts. | original pictures indicate that one had small oil leak at rad. | No impact on service. They may have been repaired by tightening bolts. |  |  | 1991-12-19
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Transformer TR |  | Small Rad | [9 empty] | 230 | 13.8 |  |  |  | McGraw Edison |  |  | TR1 | [7 empty] | 1998-07-20
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 1 | Wave Trap WT |  |  |  |  | H. Post-Insulator Mount | [6 empty] | 230 | [7 empty] | WT1 |  | Each WT is about 2' in diameter and 2' long. | Mounted on structure with CVT |  |  |  |  | 1992-01-02
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Wave Trap WT |  |  |  |  | H. Post-Insulator Mount | [6 empty] | 230 | [7 empty] | WT1 |  | Each WT is about 2' in diameter and 3' long. | Mounted on structure with CVT |  |  |  | 306 | 1992-01-02
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 2 | Wave Trap WT |  |  |  |  | H. Post-Insulator Mount | [6 empty] | 500 | [7 empty] | WT2 |  | Each WT is about 3' in diameter and 5' long. Insulators are tapered. | Mounted on lattice structure with CVT | porcelain supports failed |  |  |  | 1998-07-20
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 4 | Wave Trap WT |  |  |  |  | H. Post-Insulator Mount | [6 empty] | 500 | [7 empty] | WT2 |  | Each WT is about 3' in diameter and 5' long. Insulators are tapered. | Mounted on lattice structure with CVT |  |  |  |  | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Bus Support | [11 empty] | 500 |  |  |  | 1200 |  |  |  | BS |  | bus on site was 4 1/2 and 8 dia. al. pipe. West bus. Each bus has 6 insulator supports, each with 6 tapered sections. |  | All post insulators supporting B phase bus failed, dropping the bus. Connector between top of post insulator and bus may have been weak spot. Some units failed at connection and some had porcelain failure. This was bus B phase on west side of site. |  |  |  | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 1 | Bus Support | [11 empty] | 500 |  |  |  | 1200 |  |  |  | BS |  | East 3 phases of bus is 8". After earthquake there are 15 supports with 6 tapered elements, 7 with 2 elements, and 2 with 3 elements. |  | One insulator supporting one bus C on east side of site failed, the bus dropped but did not fall or malfunction. |  |  | 118 | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Bus Support | [11 empty] | 500 |  | 1200 | [5 empty] | BS |  | West bus, A and C phase did not fail. Bus 8" diameter pipe, with 6 insulators per bus, each with 6 tapered sections. | [5 empty] | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 |  | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#26 | PG&E | Transmission SS | [6 empty] | 0.2807 | 0.403 | 0.5254 | 0.6478 | No | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 2 | Bus Support | [11 empty] | 500 |  | 1200 | [5 empty] | BS |  | East 3 phases of bus is 8". After earthquake there are 15 supports with 6 tapered elements, 7 with 2 elements, and 2 with 3 elements. 8 insulators per bus. |  |  |  |  | 106 | 1991-12-28
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [9 empty] | 200, 230, 270, 680, | 230 |  |  |  |  | General Electric | oil |  | CB20A | [7 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 9 | Circuit Breaker CB | Dead Tank | [9 empty] | 610, 850, 860 | 230 |  |  |  |  | Westinghouse | oil |  | CB20A | [7 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 21 | Circuit Breaker CB | Dead Tank | [9 empty] | 240, 660, 800, 810, 820, 870, 880 | 230 |  |  |  |  | Allis Chalmers | oil |  | CB20A | [7 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Damaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB 4 or 6 |  | CB9 |  |  |  | Support column gasket leaks. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 7 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB 4 or 6 |  | CB9 | [7 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Transformer TR | [10 empty] | Bank 9 | 230 | 115 |  |  |  | General Electric |  | 1986 | TR1 | [7 empty] | 1998-07-17
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Transformer TR | [10 empty] | Bank 11 | 230 | 115 |  |  |  | Westinghouse |  | 1965 | TR1 | [7 empty] | 1998-07-17
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#28 | PG&E | Transmission SS | [6 empty] | 0.2064 | 0.287 | 0.367 | 0.4472 | No | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | ground motion from Paul Somerville, Mw=7.0 |  |  |  |  | Undamaged |  | 3 | Transformer TR | [10 empty] | Bank 7 | 230 | 115 |  |  |  | Westinghouse |  | 1974 | TR1 | [7 empty] | 1998-07-17
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | Air supply looked good. Lowest porcelain on CT support column failed. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 6 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7, ATB-242-43000-7 |  | CB14 |  | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | This equipment was only viewed after it was in bone yard, so specific equipment could not be associated with specific dispatch positions, and parts could not always be associated with a single phase. It is assumed that at least one support column usuall |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 24 | Circuit Breaker CB | Dead Tank | [9 empty] | 212, 222, 252, 262, 342, 372, 712, 722 | 230 |  |  |  |  | Westinghouse | Oil |  | CB20A |  | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | This equipment was only viewed after it was in bone yard, so specific equipment could not be associated with specific dispatch positions, and parts could not always be associated with a single phase. It is assumed that at least one support column usuall |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB 4 230-15000-4 |  | CB9 |  |  |  | Do not have any details on damage of these units. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 2 | Coupling Voltage Trans. CVT | [11 empty] | 230 | [7 empty] | CC1 |  |  | mounted on lattice structure that supported WT and CVT. | CVT porcelain column broke at base of column. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 1 | Coupling Voltage Trans. CVT | [11 empty] | 230 | [7 empty] | CC1 |  | may be more than one | Mounted on lattice structure with WT. There was at least one other. | how many were undamaged, and what was installation. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  | The insulators were cap&pin type (Victor) | These units were supported high on the bus support structure, they were probably CB disconnect switches. They were mounted with the porcelain in the horizontal position. | There were two failures of post insulators. |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 5 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  |  | There were one to three type of failures. In one, a weld that connects the base of the plate that is bolted to the bottom flange of the post insulator failed so that no torque could be applied to the column to change the position of the switch. There w |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  | How many undamaged switches were there and how were they mounted? | [5 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  | The insulators were cap&pin type. | These units were supported high on the bus support structure, they were probably CB disconnect switches. They were mounted with the porcelain in the horizontal position. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 4 | Lightning Arrester LA |  |  |  | TR Body Mount | [7 empty] | 230 | [7 empty] | LA1 |  |  | Mounted on body of 230/115 kV McGraw Edison TR Bank 7 |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | TR Mounted | [7 empty] | 230 | [7 empty] | LA1 |  |  | Mounted on General Electric TR Banks 5 & 6. It is not clear how they are mounted - body or boom. |  |  |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 3 | Transformer TR | [11 empty] | 115 | 60 | [6 empty] | TR |  |  | Seven TRs mounted on large elevated pads. Three mounted with bolts that were grouted in along sides of pad through large angle came lose. This was an old installation. The grout had the consistency of very weak plaster of Paris. |  | The was no impact of operations. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 4 | Transformer TR |  | Large Rad/Manif | [8 empty] | Bank 7 | 230 | 115 |  |  |  | McGraw Edison |  |  | TR1 |  | photo page 3-74 of EPRI NP-7500-SL |  | Replace seals at upper connection to stop leaking. Not sure how many leaks. I think there were 4 TRs. On return visit I thought that deformation of lower support was recorded but I could not find it in my slides. | Excavate to remove soil that had absorbed spilled oil. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  | 6 | Transformer TR |  | Med Rad/O Manif | [8 empty] | Bank 5 & 6 | 230 | 115 |  |  |  | General Electric |  |  | TR1 | [7 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 2 | Miscellaneous | [11 empty] | 115 | [9 empty] | Section of rigid bus that passes over bus support structure and forms connection between flexible bus and CB had its end casting fail. |  |  | The fallen bus fell on flexible bus of three phases. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 2 | Bus Support | [11 empty] | 230 | [7 empty] | BS |  | Hook connection between strain bus and bus support structure became unhooked and dropped bus. | [5 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 2 | Bus Support | [11 empty] | 230 | [7 empty] | BS |  | Transfer bus. |  | Post insulators supporting a section of transfer bus failed, allowing the bus to fall in one case or drop in another | The fallen bus fell on flexible bus of three phases. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Undamaged |  |  | Bus Support | [11 empty] | 230 | [7 empty] | BS |  | Transfer Bus | [5 empty] | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 1 | Miscellaneous | [11 empty] | 230 | [7 empty] | BS |  | Section of rigid bus that that connects to flexible bus to by-pass CB on top of support structure had its end casting fail, allowing rigid bus to swing and come in contact with bus support structure. |  |  | The fallen bus fell on flexible bus of three phases. |  |  | 1991-11-26
Loma Prieta | 1989-10-17 | 17:04:15 | 37.037 | 121.883 | 7 | 18.5 | Strike-Slip |  |  | 130 |  | 9 | Data from Ref. 1 pp.7&9 SM Data: USGS 38, CDMG 94, PG&E ? Aftershock data obtained at Moss Landing and Metcalf that are being analyzed. | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS | SS#39 | PG&E | Transmission SS | [6 empty] | 0.1858 | 0.256 | 0.327 | 0.3971 | No | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) |  | ground motion from Paul Somerville, Mw=7.0 | 0.2 |  |  |  | Damaged |  | 1 | Synchronous Condensor | [11 empty] | 230 | [9 empty] | Synchronous Condenser. When I visited the site, it looked like one of the units was being worked on. There was a portable nitrogen supply connected to the units. There may have been a gas leak. |  |  |  |  | 82 | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#20 | [8 empty] | 0 | [7 empty] | 0 |  |  |  | Damaged |  | 1 | Circuit Switcher CS | [10 empty] | 117 | 115 |  |  |  |  | S & C |  |  | CS |  | Circuit switcher 115 kV |  | Blew up. | CB 112 relayed on fault pressure. There was not test made. Bank was inspected, looked OK and CB closed @ 1410. At 1425 117 blew up and CB 112 isolated station. Cleared 117 and picked up one bank. |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 9 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days which CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 832 | 500 |  | 4000 |  |  | Allis Chalmers | ABM SN 11714 | 1965 | CB15A |  |  |  | Aluminum casting that supports the interrupter head failed. | Out of service for 4 days - no effect on service. |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 9 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days which CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Undamaged |  | 2 | Circuit Breaker CB | Live Tank | [9 empty] | 832 | 500 |  | 4000 |  |  | Allis Chalmers | ABM SN 11714 | 1965 | CB15A |  | seismic specification was 0.2g static horizontal. | [5 empty] | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Dead Tank | [9 empty] | 272, 282 | 230 |  |  |  |  | Westinghouse | 2300SF1500 | 1967 | CB20 | [7 empty] | 1998-06-12
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Dead Tank | [9 empty] | 292 | 230 |  |  |  |  | Pen | Oil, RHE90 | 1966 | CB20A | [7 empty] | 1998-06-12
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 822 | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications, original specifications was .2g horizontal - static | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | Interrupter head support column adjacent to CT failed - lowest ceramic member cracked. 4 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 2 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Undamaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. |  |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 922 | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | Cracked interrupter head support column adjacent to CT. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Undamaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. |  |  |  | 18 | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Undamaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. |  |  |  | 19 | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN Z 62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 1 damaged guy. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 6 hrs to repair guy at a convenient time. |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 3 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 2 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 742 | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is more rigid than x2x units. Both welded and friction clip anchorage. Installed in 1968. | 1 damaged guy - next to CT. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Undamaged |  | 8 | Circuit Breaker CB | Live Tank | [9 empty] | 842, 942 | 500 |  | 3000 |  |  | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | CB72 |  | No Seismic modifications | Rigid connection between CB and CT, CT support is more rigid than x2x units. Both welded and friction clip anchorage. Installed in 1968. | It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. |  | Undamaged |  | 6 | Circuit Breaker CB | Live Tank | [9 empty] | 732, 932 | 500 |  |  |  |  | General Eelctric | ATB 500380001K | 1968 | CB15 | [7 empty] | 1998-07-20
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  |  |  | Undamaged |  | 18 | Circuit Breaker CB | [10 empty] | 212, 222, 232, 242, 252, 262 | 230 | [5 empty] | Unknown |  | CB74 | [7 empty] | 1998-06-12
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  |  |  | Undamaged |  | 3 | Transformer TR | [10 empty] | Bank 3 A, B, C | 230 | 70 |  |  |  |  | single phase | 1967 | TR1 | [7 empty] | 1998-06-12
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 |  |  | SS#21 | PG&E | Transmission SS |  |  |  | 25 |  |  | 0.06 |  |  |  |  | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 |  |  |  | Undamaged |  | 3 | Transformer TR | [10 empty] | Bank 1 A, B, C | 500 | 230 |  |  |  |  | single phase | 1967 | TR3 | [7 empty] | 1998-06-12
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 15 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF6 |  | CB20 | [6 empty] | 137 | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [9 empty] | 382, 262, 232, 252 | 230 | [5 empty] | Oil |  | CB20A | [7 empty] | 1998-06-12
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [9 empty] | 812B | 500 |  | 3000 |  |  | Westinghouse | SF6, 500SF35000,SN 3-62405041 Seis reinforced 1973 | 1966 | CB72s | 130000 | Seismically strengthened 1973 by replacing wood tendons with fiberglass. Originally were 0.2g static horizontal. Note that SCE seismic units also have dampers. | Anchor bolts securing friction clips on 6 legs stretched or pulled out slightly. Adjacent current transformers had tit-tat-toe chair support that was flexible and there were signs of distress in cracked paint but no permanent deformations. Rigid connec | Interrupter head near CT failed explosively and with internal part of interrupter severely burned. There was not significant shifting of CB on its pad. There may have been vertical impact due to stretch or pullout of anchor bolts. Motion of CT may hav | 9 days to restore, did not cause disruption. |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 11 | Circuit Breaker CB | Live Tank | [9 empty] | 722, 822, 922, 812 A&C | 500 |  | 3000 |  |  | Westinghouse | SF6, 500SF35000,SN3-624-5041 Seis | 1966 | CB72s | 130000 | Seismically strengthened 1973 by replacing wood tendons with fiberglass. Originally were 0.2g static horizontal. Note that SCE seismic units also have dampers. | Anchor bolts securing friction clips on 6 legs stretched or pulled out slightly. Adjacent current transformers had tit-tat-toe chair support that was flexible and there were signs of distress in cracked paint but no permanent deformations. Rigid connec |  |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 15 | Circuit Breaker CB | [10 empty] | 222, 242, 212, 312,292 | 230 | [5 empty] | Unknown |  | CB74 | [7 empty] | 1998-06-12
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB6 |  | CB9 | [7 empty] | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 1 | Coupling Voltage Trans. CVT | [5 empty] | CB Mounted | [5 empty] | 230 | [7 empty] | CC1 | [6 empty] | 143 | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  |  | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | CC1 | [7 empty] | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  |  | Coupling Voltage Trans. CVT | [5 empty] | Structure/WT | [5 empty] | 230 | [7 empty] | CC1 | [7 empty] | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 5 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 500 | [7 empty] | CC5 | [7 empty] | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 12 | Current Trans. CT | [11 empty] | 500 | [7 empty] | CT5 | [7 empty] | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 24 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 | [7 empty] | DS1 | [6 empty] | 127 | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 6 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [7 empty] | DS2 |  |  | Don't know how many but there are at least 6 |  |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Damaged |  | 1 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 |  |  |  |  | General Electric 192 | 9L11AW736 Alugard | 1964 | LA1 |  | Pictures indicate that there was a short porcelain section at base with a coupling to a long upper section. | Mounted on boom on 230/115 Pennsylvania TR | The short lower porcelain member of LA that failed. | 6 hours to repair, no effect on operation at site |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  | Pictures indicate that there was a short porcelain section at base with a coupling to a long upper section. | Mounted on boom on 230/115 Pennsylvania TR |  |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 7 | Lightning Arrester LA |  |  |  | TR Body Mount | [7 empty] | 230 | [7 empty] | LA1 |  | mounted on body of 500/230 kV TR | [5 empty] | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 7 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 500 | [7 empty] | LA5 |  |  | Associated with 500/230 kV TR |  |  |  | 134 | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 8 | Transformer TR |  | Med Rad/O Manif | [9 empty] | 230 | 115 |  |  |  | Pennsylvania | Spec. 10035, sn 0-02265-5-3 | 1950 | TR1 | 211400 | Rad. elements supported from tank. C&C 94700, T&F 64400, 6970 g - 54300. | 230 LA on boom, 115 LA on rad. |  |  |  |  | 1998-07-08
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 1 | Transformer TR | [10 empty] | Bank 1, 2, 2 | 230 | 115 |  |  |  | Westinghouse | single phase | 1968 | TR1 | [7 empty] | 1998-07-08
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 1 | Transformer TR |  | Large Rad/Manif | [9 empty] | 500 | 230 |  |  |  | McGraw Edison | Spec. 13330, sn C06503-5-7 | 1968 | TR3 | 490300 | Large radiators with each element supported from maniford perp. to TR tank. 70" X 127" along TR. They are supported on non-penatrating pipe at bottom and penetrating pipe at top. There are horizontal braces at bottom but not consistant (one brace was | 230 LA on rad. |  |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 3 | Transformer TR |  | Large Rad/Manif | [9 empty] | 500 | 230 |  |  |  | General Electric | OA, FA, FO, sn D577035, -6, 7 | 1968 | TR3 | 600000 | 2 large radiators per side with each element supported from heavy box beam perp. to TR body and with non-penatrating connection with gusset plates for vert. load. Top connection is penertatng pipe. Each 142" long. There are diagonal braces at bottom, | West end of TR row. 230 kV LA installed on rad. |  |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 3 | Transformer TR |  | Large Rad/O Manif | [9 empty] | 500 | 230 |  |  |  | Westinghouse | OA, FA, FO, Core Type | 1968 | TR3 | 606000 | Large radiators with each element supported from a TR tank. Rad. on sies and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 230 LA on boom. 500 LA on independent lattice structure. Units 1, 2 and 4 from east end of site. |  |  |  |  | 1991-11-26
Morgan Hill | 1984-04-24 | 13:15 | 37.32 | 121.698 | 6.2 | 8.2 | Strike-Slip |  |  |  |  | 7 | Data from pp407 ref 1 SM Data:72 total, CDMG, USGS, CDWR, IBM (Ref 1, pp 419) MMI Map on cover of Ref 1 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ? | SS#24 | PG&E | Transmission SS | [6 empty] | 0 |  |  |  |  | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) |  |  | 0 |  |  |  | Undamaged |  | 4 | Wave Trap WT |  |  |  |  | H. Post-Insulator Mount | [6 empty] | 500 | [7 empty] | WT2 | [7 empty] | 1991-11-26
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 9 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [7 empty] | CB20 |  | ITE "watch bob" gas type | [5 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 24 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [7 empty] | CB20A |  | vertical tank type oil circuit breakers | [5 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [9 empty] | CB 912 - Palo Verde Line | 500 |  |  |  |  | Cogenel | air blast |  | CB5 |  | flexible conductors, dynamic analysis 0.5 g PGA design specification | mounted on steel A-frame w/ horizontal pressure vessel, breaker head mounted on 30 ft high columns (diagonally braced) consisted of 3 large spherical mufflers, 4 tripping resistors, 2 capacitors, 2 extinguishing chambers | completely destroyed, diagonal and vertical insulators failed, breaker heads fell |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [9 empty] | CB 712 - Palo Verde Line | 500 |  |  |  |  | Cogenel | air blast |  | CB5 |  | flexible conductors, dynamic analysis 0.5 g PGA design specification | mounted on steel A-frame w/ horizontal pressure vessel, breaker head mounted on 30 ft high columns (diagonally braced) consisted of 3 large spherical mufflers, 4 tripping resistors, 2 capacitors, 2 extinguishing chambers | completely destroyed, diagonal and vertical insulators failed, breaker heads fell |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Live Tank | [9 empty] | CB 922 | 500 |  |  |  |  | Westinghouse | puffer |  | CB73 |  | flexible conductors, dynamic analysis 0.5 g PGA design specification | no horizontal pressure vessel, no mufflers in breaker head |  |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Circuit Breaker CB | [10 empty] | CB4032 | 220 |  |  |  |  | GE | ATB4-6 SF6 |  | CB9 |  |  | supported on steel frame | 2 column insulators broken , tank damage and corona ring broken | replaced |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Circuit Breaker CB | [10 empty] | CB4102 | 220 |  |  |  |  | GE | ATB4-6 SF6 |  | CB9 |  |  | supported on steel frame | 2 column insulators shattered |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 2 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 500 |  |  |  |  | Trench Electric & GE |  |  | CC5 | [7 empty] | 1998-10-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 4 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 500 |  |  |  |  | Trench Electric & GE |  |  | CC5 | [7 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 1 | Current Trans. CT | [10 empty] | CB 922 | 500 |  |  |  |  | Alsthom |  |  | CT5 | [7 empty] | 1998-03-22
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 2 | Current Trans. CT | [10 empty] | CB 922 | 500 |  |  |  |  | Alsthom |  |  | CT5 |  |  |  | B & C broken , failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Current Trans. CT | [10 empty] | CB 912 | 500 |  |  |  |  | Alsthom |  |  | CT5 |  |  |  | A in half, B&C broken at flange, failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Current Trans. CT | [10 empty] | CB 712 | 500 |  |  |  |  | Alsthom |  |  | CT5 |  |  |  | failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 9 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 |  |  |  |  | Porter & Brown Boveri |  |  | DS1 |  |  |  | Brown Boveri failed on jaw side at base of insulators, Porter failed on hinge side in the porcelain |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 3? | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 |  |  |  | 2500 lb on hinge support, 3500 lb on jaw support | Siemens-Allis | AVB4 |  | DS1 | [7 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 15 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 500 |  |  |  |  | Porter & Brown Boveri |  |  | DS1 | [7 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | bank |  | CB 5032 | 220 | [7 empty] | DS3 |  |  | Supported on steel frame | destroyed, A phase broke at mounting flange for insulators |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | line |  | CB 5032 | 220 | [7 empty] | DS3 |  |  | Supported on steel frame | damaged, C phase out of adjustment would not open |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Bus |  | Hinds-CB 6022 | 220 | [7 empty] | DS3 |  |  | Supported on steel frame | A phase damaged, conductors from bus disconnects to bus stiffening insulators broke at base |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Disconnect Switch DS | [8 empty] | Vertical Swing |  | position no. 3, Vista #1 T/L CB 6032 | 220 |  |  |  |  | Brown Boveri | line side of CB 6032, single blade |  | DS3 |  |  | Supported on steel frame | destroyed, broke at disconect flange all three phases |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 84 | Disconnect Switch DS | [11 empty] | 220 | [7 empty] | DS3 |  |  | Supported on steel frame |  |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Lightning Arrester LA | [10 empty] | 1A Bank | 115 | [7 empty] | LA |  |  |  | destroyed, all three phases broke at base |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 2 | Lightning Arrester LA | [11 empty] | 220 | [7 empty] | LA1 | [7 empty] | 1998-03-22
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 2 | Lightning Arrester LA | [10 empty] | 4A Bank | 220 |  |  |  |  | GE | ALUGARD 9L11LBA1B |  | LA1 |  |  |  | destroyed, A & B phase broke at base |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 2 | Lightning Arrester LA | [10 empty] | 3A Bank | 220 | [7 empty] | LA1 |  |  |  | destroyed, A & B phase broke at base |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Lightning Arrester LA | [10 empty] | 2A Bank | 220 | [7 empty] | LA1 |  |  |  | destroyed, all three phases broke at base |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 1 | Lightning Arrester LA | [11 empty] | 500 |  |  |  |  | Ohio Brass | MPR Series F |  | LA5 | [7 empty] | 1998-03-22
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 9 | Lightning Arrester LA | [11 empty] | 500 |  |  |  |  | Ohio Brass | MPR Series F |  | LA5 |  |  |  | destroyed, all broken at base of porcelain, may have been caused by swinging of wave traps which they were attached to by conductors |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Potential Trans. PT | [10 empty] | Position no. 10, so. 220 kV Bus | 220 |  |  |  |  | GE | CD31023 SINGC |  | PT1 |  |  |  | destroyed, broke at base of bushing |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Potential Trans. PT | [10 empty] | Position no. 10, no. 220 kV Bus | 220 |  |  |  |  | GE | CD3123 SINGC |  | PT1 |  |  |  | destroyed, broke at base of bushing |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 4 | Potential Trans. PT | [6 empty] | Line |  |  |  |  | 500 |  |  |  |  | GE Pot Dev CC | 4CD52A505C6C |  | PT5 |  |  |  | destroyed |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 6 | Potential Trans. PT | [6 empty] | Bus |  |  |  |  | 500 | [7 empty] | PT5 |  | W. Pot. Dev Type FCA |  | destroyed |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 4 | Transformer TR | [10 empty] | 1A, 2A, 3A, 4A | 200 | 115 |  |  |  |  | three phase |  | TR2 |  |  |  | leaking oil around seals on bushings at the top of transformers, L-shaped connectors stressed beyond elestic limit at base causing transformers to walk and rock |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 1 | Transformer TR | [10 empty] | 1AA bank | 500 | 220 |  |  |  | Allis-Chalmers | single phase |  | TR3 |  |  | 500 kv bushing W Type O EBM 1675, concrete pad, anchored by steel gusset plates connected to concrete by 1" bolts and hooked over base flange | leaking oil around seals on bushings at the top of transformers, 1" bolts sheared at base causing transformers to walk (8" to 10") and rock |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Transformer TR | [10 empty] | 1AA bank | 500 | 220 |  |  |  | Westinghouse | single phase |  | TR3 |  |  | 500 kv bushing W Type O EBM 1675, concrete pad, anchored by embeded steel gusset plates hooked over base flange | leaking oil around seals on bushings at the top of transformers, L-shaped connectors stressed beyond elastic limit at base causing transformers to walk and rock |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 2 | Wave Trap WT |  |  |  |  | Hanging | [6 empty] | 500 |  |  |  |  | GE |  |  | WT2 | [7 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 2 | Wave Trap WT |  |  |  |  | Hanging | [6 empty] | 500 |  |  |  |  | GE |  |  | WT2 | [7 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 3 | Motor Operated Disconnect Switch MODS | [11 empty] | 220 |  |  |  |  | Siemens-Allis | single blade |  | MODS |  | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch |  |  |  |  | 1998-03-22
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 1 | Motor Operated Disconnect Switch MODS | [10 empty] | MOD 4041, 2A Bank | 220 |  |  |  |  | Siemens-Allis | single blade |  | MODS |  | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assembly broke off at base on A phase |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 3 | Motor Operated Disconnect Switch MODS | [10 empty] | MOD 6063 3A Bank | 220 |  |  |  |  | Siemens-Allis | single blade |  | MODS |  | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assemblies fell to ground on all three phases |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 2 | Motor Operated Disconnect Switch MODS | [10 empty] | MOD 6073 4A Bank | 220 |  |  |  |  | Siemens-Allis | single blade |  | MODS |  | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assembly broke off at base on A phase |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 2 | Bus Support | [11 empty] | 500 | [7 empty] | BS |  |  | on top of A-frame racks supporting rigid jumper bus tie | 2 insulators failed at base dropping rigid bus and twisting flexible conductors. |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 64 | Bus Support | [11 empty] | 500 | [7 empty] | BS |  | bus suspension insulators | [5 empty] | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 8 | Post Insulator PI | [11 empty] | 500 | [7 empty] | PI | [7 empty] | 1998-10-28
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 70 | Post Insulator PI | [11 empty] | 500 | [7 empty] | PI |  | supported bus conductors |  | may have been caused by slack bus conductor strung from post to post |  |  |  | 1986-07-08
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Undamaged |  | 2 | Shunt Reactor | [11 empty] | 500 |  |  |  |  | GE | OA-MS |  | SR |  |  | concrete pad, anchored by embeded steel gusset plates hooked over base flange |  |  |  |  | 1998-10-28
North Palm Springs | 1986-07-08 | 02:20:45 | 33.998 | 116.607 | 5.9 | 12 | [6 empty] | Data from pp 1, Ref. 1 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88 | SS#7 | SCE | Transmission SS | [6 empty] | 0.836 | 1.53 | 1.23 | 1.63 | Yes | Quaternary formation - alluvial fan deposits |  | Ground motion from EPRI NP-5607 | 0.55 |  |  |  | Damaged |  | 4 | Shunt Reactor | [11 empty] | 500 |  |  |  |  | GE | OA-MS |  | SR |  |  | concrete pad, anchored by embeded steel gusset plates hooked over base flange | three types of failure, 1) rocking, 2) excessive movements of reactor bushings causing oil leaks, 3) terminal connector at top of bushing pulled off |  |  |  | 1986-07-08
Pt. Mugu | 1973-02-21 | 7:46 | 34.1 | 119.8 | 5.9 | [9 empty] | SS#40 | SCE | Transmission SS | [6 empty] | 0.1158 | 0.2168 | 0.2521 | 0.239 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 54 | Circuit Breaker CB | Dead Tank | [9 empty] | 5012, 5022, 5042, 5072, 5082, 5092, 5102, 5112, 4082, 4092, 6012, 6022, 6042, 6072, 6082, 6092, 6102, 6112 | 230 | [5 empty] | Oil |  | CB20A | [7 empty] | 1998-03-22
Pt. Mugu | 1973-02-21 | 7:46 | 34.1 | 119.8 | 5.9 | [9 empty] | SS#40 | SCE | Transmission SS | [6 empty] | 0.1158 | 0.2168 | 0.2521 | 0.239 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 108 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Pt. Mugu | 1973-02-21 | 7:46 | 34.1 | 119.8 | 5.9 | [9 empty] | SS#40 | SCE | Transmission SS | [6 empty] | 0.1158 | 0.2168 | 0.2521 | 0.239 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Pt. Mugu | 1973-02-21 | 7:46 | 34.1 | 119.8 | 5.9 | [9 empty] | SS#40 | SCE | Transmission SS | [6 empty] | 0.1158 | 0.2168 | 0.2521 | 0.239 | yes | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Transformer TR | [10 empty] | 2A, 4A | 230 | 66 |  |  |  |  | three phase |  | TR2 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#1 | SCE | Transmission SS | [6 empty] | 0.065 | 0.121 | 0.173 | 0.178 | No | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 63 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#1 | SCE | Transmission SS | [6 empty] | 0.065 | 0.121 | 0.173 | 0.178 | No | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | oil |  | CB20A | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#1 | SCE | Transmission SS | [6 empty] | 0.065 | 0.121 | 0.173 | 0.178 | No | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 150 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 220 | [7 empty] | DS3 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#1 | SCE | Transmission SS | [6 empty] | 0.065 | 0.121 | 0.173 | 0.178 | No | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 24 | Lightning Arrester LA | [11 empty] | 220 | [7 empty] | LA1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#1 | SCE | Transmission SS | [6 empty] | 0.065 | 0.121 | 0.173 | 0.178 | No | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 7 | Transformer TR |  | Unit | [9 empty] | 220 | 14 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#1 | SCE | Transmission SS | [6 empty] | 0.065 | 0.121 | 0.173 | 0.178 | No | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Transformer TR | [10 empty] | 1A, 2A | 220 | 66 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#1 | SCE | Transmission SS | [6 empty] | 0.065 | 0.121 | 0.173 | 0.178 | No | Quaternary formation - soil |  | ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Transformer TR |  | Unit | [8 empty] | 1, 2, 3, 4, 5, 6 | 220 | 14 |  |  |  |  | three phase |  | TR2 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#8 | SCE | Transmission SS | [6 empty] | 0.211 | 0.337 | 0.506 | 0.489 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#8 | SCE | Transmission SS | [6 empty] | 0.211 | 0.337 | 0.506 | 0.489 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | Oil |  | CB20A | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#8 | SCE | Transmission SS | [6 empty] | 0.211 | 0.337 | 0.506 | 0.489 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 42 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  | 401, 603 and either side of 432, 422, 412, 632, 622, 612 | 220 | [7 empty] | DS3 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#8 | SCE | Transmission SS | [6 empty] | 0.211 | 0.337 | 0.506 | 0.489 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA | [11 empty] | 60 | [7 empty] | LA |  |  | How is it installed | porcelain failed. |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#8 | SCE | Transmission SS | [6 empty] | 0.211 | 0.337 | 0.506 | 0.489 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | unk | Lightning Arrester LA | [11 empty] | 60 | [7 empty] | LA |  |  | How is it installed | porcelain failed. |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#8 | SCE | Transmission SS | [6 empty] | 0.211 | 0.337 | 0.506 | 0.489 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 7 | Lightning Arrester LA | [11 empty] | 220 | [7 empty] | LA1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#8 | SCE | Transmission SS | [6 empty] | 0.211 | 0.337 | 0.506 | 0.489 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 7 | Transformer TR | [10 empty] | 4A, 3A | 220 | 66 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#18 | SCE | Transmission SS | [6 empty] | 0.13 | 0.235 | 0.342 | 0.363 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 54 | Circuit Breakers CB | Dead Tank | [9 empty] | 4142, 4122, 4112, 4102, 4097, 4062, 1052, 4042, 4032, 6142, 6122, 6112, 6102, 6097, 6062, 6052, 6042, 6032 | 220 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#18 | SCE | Transmission SS | [6 empty] | 0.13 | 0.235 | 0.342 | 0.363 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 108 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  | either side of 4142, 4122, 4112, 4102, 4097, 4062, 1052, 4042, 4032, 6142, 6122, 6112, 6102, 6097, 6062, 6052, 6042, 6032 | 220 | [7 empty] | DS2 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#18 | SCE | Transmission SS | [6 empty] | 0.13 | 0.235 | 0.342 | 0.363 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 15 | Lightning Arrester LA | [11 empty] | 220 | [7 empty] | LA1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#18 | SCE | Transmission SS | [6 empty] | 0.13 | 0.235 | 0.342 | 0.363 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 5 | Transformer TR | [10 empty] | 1A, 2A, 3A, 4A | 220 | 66 |  |  |  |  | 3 phase |  | TR2 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#18 | SCE | Transmission SS | [6 empty] | 0.13 | 0.235 | 0.342 | 0.363 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Undamaged |  | 1 | Synchronous Condensor | [11 empty] | 230 | [9 empty] | Synchronous Condenser |  | misalignment causing loss of bearing pressure |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#18 | SCE | Transmission SS | [6 empty] | 0.13 | 0.235 | 0.342 | 0.363 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville, Mw=6.6 |  |  |  |  | Damaged |  | 3 | Synchronous Condensor | [11 empty] | 230 | [9 empty] | Synchronous Condenser |  | misalignment causing loss of bearing pressure. Some could continue to run. | one replace bearing and others realign. |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 39 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | Oil |  | CB20A | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 5 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB |  | CB9 |  | Model not shown in data. | [5 empty] | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB |  | CB9 |  | Model not shown in data. |  | leaking support column gaskets | N restored Feb 13, S restored Feb 26 |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 102 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-03-22
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Synchronous Condensor | [11 empty] | 230 | [9 empty] | Synchronous Condensers |  | loss of pressure, misaligned and bearing damage | realign bearings |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#19 | SCE | Transmission SS | [6 empty] | 0.097 | 0.178 | 0.257 | 0.269 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | unk | Synchronous Condensor | [11 empty] | 230 | [9 empty] | Synchronous Condensers |  |  |  |  | 280 | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.141 | 0.251 | 0.365 | 0.394 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Synchronous Condensor | [11 empty] | 230 | [9 empty] | synchronous condenser |  | loss of oil pressure |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.141 | 0.251 | 0.365 | 0.394 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  |  | Synchronous Condensor | [11 empty] | 230 | [9 empty] | synchronous condenser | [5 empty] | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | Misc | SCE | Transmission SS | [6 empty] | 0 | [11 empty] | Damaged |  | 9 | Circuit Breaker CB | [11 empty] | 16 | [7 empty] | CB |  |  |  | 6 damaged bushings at Solemint and 3 flash overs at Saugus |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | Misc | SCE | Transmission SS | [6 empty] | 0 | [11 empty] | Damaged |  | 4 | Disconnect Switch DS | [11 empty] | 60 | [7 empty] | DS |  |  |  | Disconnect switches missaligned at Citrus SS and porcelain damage at Newhall |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | Misc | SCE | Transmission SS | [6 empty] | 0 | [11 empty] | Damaged |  |  | Miscellaneous | [11 empty] | 230 | [11 empty] | Several transmission towers on several lines had to have footings or foundations compacted. While some were under construction, most were existing in-service towers. There was no disruption from these failures. |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | H. Swing-Tripod |  |  | 230 | [7 empty] | DS3 |  |  | use of tripod support | post insulator failed at base. In falling it pulled the bayonet and corona ring wich burned the operating rod. This is refered to as secondary damage. | Control rod and 3 post insulators were replaced. |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | H. Swing-Tripod |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  |  |  | Broken post insulator on line side. Unit opened and reclosed with bayonet on top of the bell on the female half of disconnect. | Replace insulator. |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  |  | Broken post insulator on line side. Reported as secondary damage. Need to review station for assessment. | Replace insulator. |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | unk | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | unk | Disconnect Switch DS | [8 empty] | H. Swing-Tripod |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 230 | [7 empty] | LA1 |  |  | From picture, the LA appears to be on line between OCB and DS, an unusal situation. | porcelain failed at base |  |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | Free Standing | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-10-29
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | 60 | [6 empty] | TR1 |  |  |  | Shifted on transfer car and slipped its rail chocks about 6 inches |  |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 | 60 | [6 empty] | TR1 |  |  |  | 66 kV bushing cracked, fell over and cracked bowl on its top. |  |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 5 | Transformer TR | [11 empty] | 230 | 60 | [6 empty] | TR1 |  |  |  | Four units sheared anchor bolts on one side and shifted 1 to 2 inches |  |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Capacitor Racks CR | [11 empty] | 16 | [11 empty] | support insulator broke. Rack pulled towards bus about 4" and three bus side bushings on 16 kV capacitor PCB flashed over and were replaced. |  |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#41 | SCE | Transmission SS | [6 empty] | 0.536 | 0.903 | 1.379 | 1.566 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Bus Support | [11 empty] | 60 | [7 empty] | BS |  | Transfer bus on 2A Bank |  | Fitting on transfer bus support failed allowing one end of bus to fall. Porcelain did not fail. |  |  |  | 1991-12-06
San Fernando | 1971-02-09 | 6:00:42 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S |  |  | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71 | SS#44 | LADWP | Transmission SS | [10 empty] | No | Quaternary formation - soil | [6 empty] | Undamaged |  | 0 | Circuit Breaker CB | [11 empty] | 230 |  |  |  |  | GE | ATB |  | CB9 | [7 empty] | 1999-03-25
San Fernando | 1971-02-09 | 6:00:42 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S |  |  | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71 | SS#44 | LADWP | Transmission SS | [10 empty] | No | Quaternary formation - soil | [6 empty] | Damaged |  | 33 | Circuit Breaker CB | [11 empty] | 230 |  |  |  |  | GE | ATB |  | CB9 | [7 empty] | 1999-03-25
San Fernando | 1971-02-09 | 6:00:42 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S |  |  | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71 | SS#44 | LADWP | Transmission SS | [10 empty] | No | Quaternary formation - soil | [6 empty] | Undamaged |  | 2 | Potential Trans. PT | [6 empty] | Post Mounted |  |  |  |  | 230 | [7 empty] | PT1 | [7 empty] | 1999-03-25
San Fernando | 1971-02-09 | 6:00:42 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S |  |  | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71 | SS#44 | LADWP | Transmission SS | [10 empty] | No | Quaternary formation - soil | [6 empty] | Damaged |  | 3 | Potential Trans. PT | [6 empty] | Post Mounted |  |  |  |  | 230 | [7 empty] | PT1 |  |  |  | remained on supports with damage to oil seals, terminal taps and base connections |  |  |  | 1999-03-25
San Fernando | 1971-02-09 | 6:00:42 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S |  |  | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71 | SS#44 | LADWP | Transmission SS | [10 empty] | No | Quaternary formation - soil | [6 empty] | Damaged |  | 7 | Potential Trans. PT | [6 empty] | Post Mounted |  |  |  |  | 230 | [7 empty] | PT1 |  |  |  | broke from steel post support pedestal and fell to ground |  |  |  | 1999-03-25
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | GE | ATB |  | CB15 | [7 empty] | 1998-10-28
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 48 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF6 |  | CB20 | [7 empty] | 1998-10-28
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 9 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | Westinghouse | SF6 non-seismic |  | CB72 | [7 empty] | 1998-10-28
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | Westinghouse | SF6 non-seismic |  | CB72 |  | Vincent is not on data sheets |  | Individual data is not vailable. 3 porcelain columns failed, 2 columns cracked of the 9 columns, 10 of 18 porcelain guys failed. 5 of 9 twisted clockwise as view from above. | 41 days before spares could be obtained. |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 6 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | Westinghouse | SF6 non-seismic |  | CB72 |  | Vincent is not on data sheets |  | 4 porcelain guys on N and 7 guys on S failed. | Guy damage would not effect operation. Units were repaired and put back into service within 48 hrs. |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 96 | Disconnect Switch DS | [11 empty] | 230 | [7 empty] | DS3 | [7 empty] | 1998-10-08
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [11 empty] | 500 | [7 empty] | DS1 |  | Vincent is not on data sheets. What is type? | How is it installed? | Post insulator failed. Unit out of alignment. |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 17 | Disconnect Switch DS | [11 empty] | 500 | [7 empty] | DS1 |  | Probably don't have all DS1 | How is it installed? |  |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA | [11 empty] | 500 | [7 empty] | LA5 |  | Vincent is not on data sheets | How is it installed? | porcelain failed. |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 10 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-10-28
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 24 | Lightning Arrester LA | [11 empty] | 500 | [7 empty] | LA5 |  | Vincent is not on data sheets | How is it installed? |  |  |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 8 | Transformer TR | [11 empty] | 500 | 230 | [6 empty] | TR3 | [7 empty] | 1998-10-28
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 500 | 230 | [6 empty] | TR3 |  | Vincent is not on data sheets |  | Radiator leak. | restoration? |  |  | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damage | Yes | 1 | Transformer TR | [11 empty] | 500 | 230 | [6 empty] | TR3 |  | Vincent is not on data sheets |  | LA damaged radiator fan. |  |  | 261 | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Bus Support | [11 empty] | 500 | [7 empty] | BS |  | Bus support | How is it installed? | 2 post insulators failed. How many did not fail? |  |  | 266 | 1991-12-10
San Fernando | 1971-02-09 | 6:00:41 | 34.412 | 118.4 | 6.4 | 13 | Thrust | N65W | 55NE |  | N40W, 37.7 S | 11 | Data from pp. 13& 49 Ref. 1, MMI Map on pp 24, Ref. 1 SM Data 241 SM Records,pp. 325, Ref. 1 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71 | SS#45 | SCE | Transmission SS | [6 empty] | 0.17 | 0.285 | 0.418 | 0.387 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 106 | Bus Support | [11 empty] | 500 | [7 empty] | BS |  | Bus support | How is it installed? | 2 post insulators failed. How many did not fail? |  |  |  | 1991-12-10
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | Oil |  | CB20A | [7 empty] | 1998-03-22
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Undamaged |  | 36 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Undamaged |  | 12 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Undamaged |  | 6 | Potential Trans. PT | [6 empty] | Low Seismic |  |  |  |  | 230 | [7 empty] | PT1 | [7 empty] | 1998-03-22
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 | 60 |  |  |  | General Electric | 8275998 |  | TR1 |  | Single phase 220/66 kV TR. |  | 220 bushing gasket leaks. Anchorage was distressed. | Replace 220 kV bushing on 220/66 kV B phase TR. |  |  | 1991-12-07
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Undamaged |  | 3 | Transformer TR | [11 empty] | 230 | 60 |  |  |  | General Electric | 8276000, -1, -2 |  | TR1 |  | Single phase 220/66 kV TRs. | [5 empty] | 1991-12-07
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Undamaged |  | 2 | Transformer TR | [11 empty] | 230 | 60 |  |  |  | General Electric | 8275997, -9 |  | TR1 |  | Single phase 220/66 kV TRs. | [5 empty] | 1991-12-07
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Damaged |  | 3 | Transformer TR | [11 empty] | 230 | 60 |  |  |  | Westinghouse | 3418517, -8, -9 |  | TR1 |  | Single phase 220/66 kV TRs. |  | 220 bushing gasket leaks. Anchorage was distressed. | Replace each 220 kV bushing on each single phase 220/66 kV TR. |  |  | 1991-12-07
Santa Barbara | 1978-08-13 | 22:54:52 | 34.37 | 119.717 | 5.1 | 12.5 | Reverse Oblique | [5 empty] | Data from pp 1, Ref.1 SM Data: 11 from CDMG 8, USGS 1, US Bureau op Reclamation 1, SCE 1 (Ref 1) | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3) | SS#13 | SCE | Transmission SS | [6 empty] | 0.26 |  |  |  | Yes | Tertiary formation - soft rock |  |  | 0.28 |  |  |  | Damaged |  | 3 | Transformer TR | [11 empty] | 230 | 60 |  |  |  | Westinghouse | 3772575, 4088092,-3 |  | TR1 |  | Single phase 220/66 kV TRs. |  | 220 bushing gasket leaks. Anchorage was distressed. | Replace each 220 kV bushing on each single phase 220/66 kV TR. |  |  | 1991-12-07
Sierra Madre | 1991-06-28 | 7:43 | 34.26 | 118 | 5.8 | 11 | Thrust | [7 empty] | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | [5 empty] | 0 |  |  |  |  | Quaternary formation - soil |  |  | 0 |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  |  |  | One of the outside interrupter head bushing blew. From slack that was available it appears that head moved about 12". |  |  |  | 1991-11-26
Sierra Madre | 1991-06-28 | 7:43 | 34.26 | 118 | 5.8 | 11 | Thrust | [7 empty] | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | [5 empty] | 0 |  |  |  |  | Quaternary formation - soil |  |  | 0 |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  |  |  | Crack at sandring allowed SF6 to leak out. | Lower porcelain member had to be replaced. |  |  | 1991-11-26
Sierra Madre | 1991-06-28 | 7:43 | 34.26 | 118 | 5.8 | 11 | Thrust | [7 empty] | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | [5 empty] | 0 |  |  |  |  | Quaternary formation - soil |  |  | 0 |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  |  |  | Porcelain interrupter head support columns failed. | Dead tank replacement unit used. |  |  | 1991-11-26
Sierra Madre | 1991-06-28 | 7:43 | 34.26 | 118 | 5.8 | 11 | Thrust | [7 empty] | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | [5 empty] | 0 |  |  |  |  | Quaternary formation - soil |  |  | 0 |  |  |  | Undamaged |  | 7 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 | [7 empty] | 1998-04-02
Sierra Madre | 1991-06-28 | 7:43 | 34.26 | 118 | 5.8 | 11 | Thrust | [7 empty] | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | [5 empty] | 0 |  |  |  |  | Quaternary formation - soil |  |  | 0 |  |  |  | Undamaged |  | 2 | Transformer TR |  | 3 phase | [9 empty] | 230 | [7 empty] | TR2 | [7 empty] | 1998-10-09
Sierra Madre | 1991-06-28 | 7:43 | 34.26 | 118 | 5.8 | 11 | Thrust | [7 empty] | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | [5 empty] | 0 |  |  |  |  | Quaternary formation - soil |  |  | 0 |  |  |  | Undamaged |  | 30 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-04-02
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 1600 |  |  | General Electric | ATB7 | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 1600 |  |  | General Electric | ATB7 | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | Only one of the gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 3000 |  |  | General Electric | ATB7 | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Interrupter head support column failed (column w/o CT) | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 3000 |  |  | General Electric | ATB7 | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 3000 |  |  | General Electric | ATB7 (isolated) | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. Unit mounted on 3/4" elastomer pad | Only one gaskets on the 2 interrupter head bushings that were connected to each other blew. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Undamaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 3000 |  |  | General Electric | ATB7 (isolated) | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. Unit mounted on sock isolators of |  | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 3000 |  |  | General Electric | ATB7 | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 1600 |  |  | General Electric | ATB7 | 1971 | CB14 |  | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Undamaged |  | 7 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  | 1600 |  |  | General Electric | ATB7 | 1971 | CB14 |  | Same as for damaged units | Same as for damaged units |  |  |  |  | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damage | Yes | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [5 empty] | low design |  | DS2 | [7 empty] | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Undamaged |  | 77 | Disconnect Switch DS | [8 empty] | Vertical Swing |  |  | 230 | [5 empty] | low design |  | DS2 | [7 empty] | 1998-04-09
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Undamaged |  | 24 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-04-09
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Damaged |  | 1 | Transformer TR |  | Large Rad/Manif | [9 empty] | 220 | [5 empty] | three phase |  | TR2 |  |  | Well anchored | Minor oil leak at top connection of radiator to tank. |  |  | 124 | 1991-11-26
Tejon Ranch | 1988-06-10 | 16:06 | 34.943 | 118.737 | 5.2 | 8.1 | [6 empty] | Data From pp791, Ref. 1 | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812 | SS#9 | CDWR | Transmission SS | [6 empty] | 0.1 |  |  |  | Yes | Firm | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 |  | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | Undamaged |  | 7 | Transformer TR |  | Large Rad/Manif | [9 empty] | 220 | [5 empty] | three phase |  | TR2 |  |  | Well anchored |  |  |  | 125 | 1991-11-26
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 63 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB4 |  | CB9 |  |  |  | CT leak on C phase | Completed 10/2.87 @ 0339 |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric? | ATB4? |  | CB9 |  |  | middle phase | Leaking nin-CT column | Completed 10/5/87 @ 1200. Note that it was after aftershock. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 10 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB 4-6 |  | CB9 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 150 | Disconnect Switch DS | [8 empty] | Horizontal |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-23
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 24 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-23
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 7 | Transformer TR |  | Unit | [9 empty] | 230 | 14 |  |  |  |  | single phase, unit |  | TR1 | [7 empty] | 1998-03-24
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 5 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | single phase |  | TR1 |  |  |  | nitrogen leak due to ruptured diaphram. | Completed 10/2/87 @ 0607. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#1 | SCE | Power Station | [6 empty] | 0.086 | 0.175 | 0.217 | 0.169 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Transformer TR |  | Unit | [9 empty] | 230 | 14 |  |  |  |  | three phase, unit |  | TR2 | [7 empty] | 1998-03-23
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 17 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Westinghouse and ITE | 2300SF15000/20000-25 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Westinghouse | 2300SF15000/20000-30 |  | CB20 |  |  |  | not known | to be replaced |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 18 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Allis Chalmers | oil |  | CB20A | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 5 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | functional immediately after eq, EPRI report indicates all had leaking seals |  |  |  | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | porcelain column shattered | to be rebuilt |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 84 | Disconnect Switch DS | [8 empty] | Horizontal |  |  | 230 | [7 empty] | DS3 |  | frame mounted | [5 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | 3 o spare |  | TR2 |  | rail mounted, steel strap welded to TR and bolted to concrete base mat | [5 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | Allis Chalmers | 1-0140-24784-1,-3;2-0102-9162-3, 7 |  | TR1 |  | rail mounted, steel strap welded to TR and bolted to concrete base mat | [5 empty] | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | General Electric | 3o D572975 |  | TR2 |  | rail mounted, steel strap welded to TR and bolted to concrete base mat | [5 empty] | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | [5 empty] | 0.198 | 0.383 | 0.466 | 0.385 | No | Quaternary formation - soft alluvium |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | Pennsylvania | 3o 01823-5-1 |  | TR2 |  | rail mounted, steel strap welded to TR and bolted to concrete base mat |  | Leaking 230 kV bushings. 2 or 3 bushings | Replaced "O" rings. Restored 11/2/87 @ 1630 |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | Leak in non-CT column | Completed 10/3/87 @ 0227 |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | Leak in non-CT column | Completed 10/4/87 @ 1654 |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB4 |  | CB9 |  | Written summary list ATB4 but data sheet gives W +M |  | 1 CT column | Completed 10/6/87 @ 2100. Note that repair was done after aftershock. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | Leaks in CT columns |  |  | 291.235 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | Leaks in CT columns | Completed 10/3/87 @ 0227 |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 10 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB4 |  | CB9 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB4 230-20000-6Y20 |  | CB9 |  | Written summary list ATB4 but data sheet suggests ATB6 |  | Leak in 2 non-CT column and 3 CT columns | Completed 10/6/87 @ 2100. Note that repair was done after aftershock. |  | 239 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 11 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB4 230-20000-6Y20 |  | CB9 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 66 | Disconnect Switch DS | [8 empty] | Horizontal |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 9 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | [5 empty] | 0.141 | 0.273 | 0.344 | 0.285 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | General Electric | three phase |  | TR2 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.224 | 0.408 | 0.498 | 0.407 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.224 | 0.408 | 0.498 | 0.407 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | oil |  | CB20A | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.224 | 0.408 | 0.498 | 0.407 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 42 | Disconnect Switch DS | [8 empty] | Horizontal |  |  | 220 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.224 | 0.408 | 0.498 | 0.407 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 7 | Lightning Arrester LA | [11 empty] | 220 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#8 | SCE | Transmission SS | [6 empty] | 0.224 | 0.408 | 0.498 | 0.407 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 7 | Transformer TR | [11 empty] | 220 | 66 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 60 | [7 empty] | CB |  | What type of equipment |  | Topping up needed but no leak found suggests that there was a leak that was self healing |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Live Tank | [10 empty] | 220 |  |  |  |  | General Electric | ATB7 |  | CB14 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | oil |  | CB20A | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Live Tank | [10 empty] | 220 |  |  |  |  | General Electric | ATB 4-6 |  | CB9 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 66 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 220 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 220 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#10 | SCE | Transmission SS | [6 empty] | 0.12 | 0.251 | 0.311 | 0.235 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Transformer TR | [11 empty] | 220 | 66 |  |  |  |  | three phase |  | TR2 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#15 | SCE | Transmission SS | [6 empty] | 0.186 | 0.328 | 0.427 | 0.356 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#15 | SCE | Transmission SS | [6 empty] | 0.186 | 0.328 | 0.427 | 0.356 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 30 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#15 | SCE | Transmission SS | [6 empty] | 0.186 | 0.328 | 0.427 | 0.356 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#15 | SCE | Transmission SS | [6 empty] | 0.186 | 0.328 | 0.427 | 0.356 | No | Mesozoic formation - hard rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 60 | [7 empty] | CB |  | Are there 66 kV SF6 CBs? |  | Ruptured releif valve |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  |  |  | non-CT columns leaking. crcked insulator. | 17 week lead time. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  |  |  | 2 non-CT columns leaking. | complete 10/2/87 @ 2327 |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  |  |  | 2 non-CT columns leaking. | complete 10/2/87 @ 1601 |  | 247 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 10 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  |  |  | There may be others that are not damaged. |  |  |  | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | oil |  | CB20A | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 78 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#16 | SCE | Transmission SS | [6 empty] | 0.122 | 0.228 | 0.292 | 0.258 | Yes | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | three phase |  | TR2 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 | [7 empty] | CB9 |  |  |  | Topping up needed but no leak found suggests that there was a leak that was self healing |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 36 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 23 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB 4-6 |  | CB9 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 120 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 9 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 60 | [7 empty] | TR |  | Not sure of voltage | [5 empty] | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Transformer TR | [11 empty] | 60 | [7 empty] | TR |  | Not sure of voltages |  | Chipped bushing |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#17 | SCE | Transmission SS | [6 empty] | 0.112 | 0.234 | 0.291 | 0.222 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | three phase |  | TR2 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Damaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB4 230-20000-0-20? |  | CB9 |  | Note model no. indicated as Westinghouse. |  | 2 interrupter head bushings leaking, 1 CT and 1 non 0CT columns leaking. | repairs 60% complete 10/5/87. Note that repairs were not colpleted until after the aftershock. |  | 245 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 39 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF6 |  | CB20 | [7 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | oil |  | CB20A | [7 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 3 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB4 230-20000-0-20? |  | CB9 | [7 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 102 | Disconnect Switch DS | [8 empty] | Low Design - Horizontal |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 6 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | single phase |  | TR1 | [7 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#19 | SCE | Transmission SS | Long Beach | [5 empty] | 0.259 |  |  |  | Yes | soft alluvium - Quaternary formation |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | three phase |  | TR2 | [7 empty] | 1998-07-01
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#22 | SCE | Transmission SS | Chandler Blvd & Cordova, Burbank | [5 empty] | 0.111 | 0.227 | 0.288 | 0.215 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Circuit Breaker CB | [11 empty] | 60 | [7 empty] | CB |  | What type of CB? |  | Cracked 66 kV bushing. |  |  | 212 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 36 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Westinghouse | 2300SF15000/20000-25 |  | CB20 | [7 empty] | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | leaking support column gasket. How many phases out? | Three days 14 hrs to repair |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. |  | 189 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 17 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | functional immediately after earthquake, EPRI report indicates that all CBs eventually developed leaks |  |  |  | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. Restored 10/4/87 @ 0330 |  | 186 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB5 230-20000-5-20 |  | CB9 |  |  |  | leaking support column gasket. How many phases out? | Three days 10 hrs to repair. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 120 | Disconnect Switch DS | [8 empty] | Horizontal |  |  | 230 | [7 empty] | DS3 |  |  | frame mounted |  |  |  |  | 1998-03-22
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA | [11 empty] | 230 | [7 empty] | LA1 |  |  | How was it installed? | Failed porcelain column | Can be restored by 10/10 (9 days) working 24 hr shift if part arrives. |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 5 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#23 | SCE | Transmission SS | Rosemead | [5 empty] | 0.22 | 0.475 | 0.544 | 0.409 | No | Quaternary formation - firm soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | General Electric | 3o D582895, D596229 |  | TR2 |  |  | Welded to embedded steel on mats |  |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#27 | SCE | Transmission SS | 13300 Mulberry Av, Whittier | [5 empty] | 0.226 | 0.448 | 0.531 | 0.45 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Capacitor Racks CR | [11 empty] | 12 | [10 empty] | How is it mounted? |  |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#29 | SCE | Transmission SS | 1315 S Garfield Av, Monterey Park | [5 empty] | 0.414 | 0.662 | 0.937 | 0.964 | No | Tertiary formation - soft rock |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Bus Support | [11 empty] | 60 | [7 empty] | BS |  |  |  | 4 post insulators for bus supports damaged. | Replaced 10/3/87 @ 2010 |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#30 | SCE | Transmission SS | La Habra | [5 empty] | 0.408 |  |  |  | Yes | Quaternary formation - soil |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 21 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Allis Chalmers | oil |  | CB20A | [7 empty] | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#30 | SCE | Transmission SS | La Habra | [5 empty] | 0.408 |  |  |  | Yes | Quaternary formation - soil |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 48 | Disconnect Switch DS | [8 empty] | Horizontal |  |  | 230 | [7 empty] | DS3 |  |  | frame mounted |  |  |  |  | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#30 | SCE | Transmission SS | La Habra | [5 empty] | 0.408 |  |  |  | Yes | Quaternary formation - soil |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 10 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#30 | SCE | Transmission SS | La Habra | [5 empty] | 0.408 |  |  |  | Yes | Quaternary formation - soil |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 4 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | Allis Chalmers | single phase |  | TR1 |  |  | anchored by gussets welded to embedded steel |  |  |  |  | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#30 | SCE | Transmission SS | La Habra | [5 empty] | 0.408 |  |  |  | Yes | Quaternary formation - soil |  | PGA from EPRI NP-7126 |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | Westinghouse | 220000-072000 5066610 |  | TR1 |  |  | anchored by gussets welded to embedded steel |  |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#30 | SCE | Transmission SS | La Habra | [5 empty] | 0.408 |  |  |  | Yes | Quaternary formation - soil |  | PGA from EPRI NP-7126 |  |  |  |  | Damaged |  | 2 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | Westinghouse | 220000-072000 506668, -9 |  | TR1 |  |  | anchored by gussets welded to embedded steel | functional, oil leaks at radiator flange. |  |  | 187 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites | SS#30 | SCE | Transmission SS | La Habra | [5 empty] | 0.408 |  |  |  | Yes | Quaternary formation - soil |  | PGA from EPRI NP-7126 |  |  |  |  | Damaged |  | 3 | Transformer TR | [11 empty] | 230 | 66 |  |  |  | Westinghouse | 220000-072000 5069946, -7, -8 |  | TR1 |  |  | anchored by gussets welded to embedded steel | functional, oil leaks at radiator flange. |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#32 | SCE | Transmission SS | 12300 Florence Av, Santa fe Springs | [5 empty] | 0.202 | 0.39 | 0.457 | 0.392 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA | [11 empty] | 60 | [7 empty] | LA |  |  | How is it mounted? | Failure of porcelain. What voltage. What is significance of "Painted Bushing Cap"? |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#32 | SCE | Transmission SS | 12300 Florence Av, Santa fe Springs | [5 empty] | 0.202 | 0.39 | 0.457 | 0.392 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  |  | Lightning Arrester LA | [11 empty] | 60 | [7 empty] | LA |  |  | How is it mounted? | . What voltage. What is significance of "Painted Bushing Cap"? |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#42 | SCE | Transmission SS | 8320 Rex Rd, Pico Rivers | [5 empty] | 0.235 | 0.486 | 0.575 | 0.446 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Bus Support | [19 empty] | BS |  |  |  | Fitting on transfer bus broke?, What voltage? |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#43 | SCE | Transmission SS | 11523 Paramount Blvd, Downey | [5 empty] | 0.211 | 0.41 | 0.514 | 0.405 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 60 | [7 empty] | TR |  | What type of TR? |  | Leaking 66 kV bushing. |  |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#46 | SCE | Transmission SS | [6 empty] | 0.232 | 0.469 | 0.575 | 0.478 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Need manufacturer |  |  | CB20A |  |  |  | Leaking bushings | Can be restored by 10/3 23:55 (2 Days 16 hrs). 1200 amp bushing was used instead of 1600 amp bushing as spare was not available. |  | 197 | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#46 | SCE | Transmission SS | [6 empty] | 0.232 | 0.469 | 0.575 | 0.478 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 23 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | oil |  |  | CB20A | [7 empty] | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#46 | SCE | Transmission SS | [6 empty] | 0.232 | 0.469 | 0.575 | 0.478 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 57 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#46 | SCE | Transmission SS | [6 empty] | 0.232 | 0.469 | 0.575 | 0.478 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 9 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 |  |  | How were LA installed? |  |  |  |  | 1998-03-25
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#46 | SCE | Transmission SS | [6 empty] | 0.232 | 0.469 | 0.575 | 0.478 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 | 60 |  |  |  |  | three phase |  | TR2 |  | What type of TR: Radiator size and mounting, LA mounting, No. of Phases? |  | What was damage to bushings? | There was not disruption of service due to bushing damage. Was it repaired? |  |  | 1991-12-08
Whittier Narrows | 1987-10-01 | 7:42:20 | 34.05 | 118.08 | 5.9 | 14 | Strike-Slip | 90 |  |  |  | 8 | MMI map pp 5 in Ref 1., CDMG got 101 stations with S-M records and USGS got 20, SCE ot ? and LADWP got ? | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357 | SS#46 | SCE | Transmission SS | [6 empty] | 0.232 | 0.469 | 0.575 | 0.478 | No | Quaternary formation - soil |  | Ground motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Transformer TR | [11 empty] | 230 | 60 |  |  |  |  | three phase |  | TR2 | [7 empty] | 1998-03-25
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.2844 | 0.4526 | 0.7116 | 0.6638 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  | The boom was moderate length and had small gussets to stiffen the boom-TR connection. | Installed on three porcelain standoffs. There was almost no slack between bushing and LA and between LA and bus support column. | Cracked at base. Hinge is consistent with pull on bus. |  |  | 374 | 1998-09-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.2844 | 0.4526 | 0.7116 | 0.6638 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 20 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  | The boom was moderate length and had small gussets to stiffen the boom-TR connection. | Installed on three porcelain standoffs. There was almost no slack between bushing and LA and between LA and bus support column. |  |  |  | 375 | 1998-09-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.2844 | 0.4526 | 0.7116 | 0.6638 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Transformer TR | [11 empty] | 230 |  |  |  |  | Hitachi |  |  | TR2 |  | 3-phase, Bushings mounted on top of tall cylinders. |  | Three of the six bushings leaked, were leaking and had to be removed to restore. One bushing had a hairline crack along its length. These are draw-type bushings and the cracked unit had a tight fit to the draw mechanism. | The three bushings that had shifted and were leaking were repaired in the bushing shop. |  | 371 | 1998-09-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.2844 | 0.4526 | 0.7116 | 0.6638 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 |  |  |  |  | Westinghouse |  |  | TR2 |  | 3 phase |  | The TR case, about 3-1/2' above base had a crack in a weld at a corner. | Using a center punch, metal was moved to close the crack. |  | 373 | 1998-07-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.2844 | 0.4526 | 0.7116 | 0.6638 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Transformer TR | [11 empty] | 230 |  |  |  |  | Westinghouse |  |  | TR2 |  | 3 phase |  |  |  |  | 372 | 1998-09-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.2844 | 0.4526 | 0.7116 | 0.6638 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | [7 empty] | TR2 |  | 3 phase | [5 empty] | 2002-07-18
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from TCLEE Mongraph 8, 1995 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 15 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB7 |  | CB14 |  | See TCLEE Mongraph 8, some equipment missing from drawings | [5 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 0 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF-6 |  | CB20 |  | See TCLEE Mongraph 8, some equipment missing from drawings | [5 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Undamaged |  | 45 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 | [5 empty] | SF-6 |  | CB20 |  | See TCLEE Mongraph 8, some equipment missing from drawings | [5 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 7 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB 4-6 |  | CB9 |  | See TCLEE Mongraph 8, some equipment missing from drawings | [5 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Undamaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 230 |  |  |  |  | General Electric | ATB 4-6 |  | CB9 |  | See TCLEE Mongraph 8, some equipment missing from drawings | [5 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 19 | Current-Voltage Transformer | [11 empty] | 230 | [7 empty] | CC1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Undamaged |  | 26 | Current-Voltage Transformer | [11 empty] | 230 | [7 empty] | CC1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 75 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 |  |  |  | only required adjustment |  |  |  | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 42 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 |  |  |  | visibly damaged |  |  |  | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 21 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 |  |  |  | seriously damaged |  |  |  | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 0 | Potential Trans. PT | [6 empty] | Low Seismic |  |  |  |  | 230 | [7 empty] | PT1 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Undamaged |  | 6 | Potential Trans. PT | [6 empty] | Low Seismic |  |  |  |  | 230 | [7 empty] | PT1 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Damaged |  | 0 | Wave Trap WT | [11 empty] | 230 | [7 empty] | WT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#31 | SCE | Transmission SS | [6 empty] | 0.44 |  |  |  | Yes | Quaternary formation - soil |  | PGA from Earthquake Spectra 95-03, April 1995 |  |  |  |  | Undamaged |  | 13 | Wave Trap WT | [11 empty] | 230 | [7 empty] | WT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 0 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Mitsubishi | SF6 |  | CB20 |  | Qualified by a 0.5g 10 cycle sine-beat shake table test | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 87 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Mitsubishi | SF6 |  | CB20 |  | Qualified by a 0.5g 10 cycle sine-beat shake table test | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 14 | Current-Voltage Transformer | [11 empty] | 230 | [7 empty] | CC1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 40 | Current-Voltage Transformer | [11 empty] | 230 | [7 empty] | CC1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Current-Voltage Transformer | [5 empty] | Post Mounted |  |  |  |  | Bank H, A phase | 500 | [7 empty] | CC5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Current-Voltage Transformer | [5 empty] | Post Mounted |  |  |  |  | Banks G1 & G2, A phase | 500 | [7 empty] | CC5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Current-Voltage Transformer | [5 empty] | Post Mounted |  |  |  |  | Banks G1 & G2, B phase | 500 | [7 empty] | CC5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Current-Voltage Transformer | [5 empty] | Post Mounted | [5 empty] | 500 | [7 empty] | CC5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  | Bank H, C phase | 500 | [7 empty] | DS1 |  | Qualified by a 0.5g 10 cycle sine-beat shake table test |  | 2 columns failed at base, Damage caused by interaction from adjacent equipment, pull over by WT |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  | Bank H, B phase | 500 | [7 empty] | DS1 |  | Qualified by a 0.5g 10 cycle sine-beat shake table test |  | 1 column failed at base, Damage caused by interaction from adjacent equipment, pulled over by WT |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Vertical Swing |  | Bank H, A phase | 500 | [7 empty] | DS1 |  | Qualified by a 0.5g 10 cycle sine-beat shake table test |  | 2 columns failed at base, Damage caused by interaction from adjacent equipment, pulled over by WT |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | Banks G1 & G2, A phase | 500 | [7 empty] | DS1 |  | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | both tripods failed |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | Banks G1 & G2, B phase | 500 | [7 empty] | DS1 |  | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 1 tripod failed |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | Banks G1 & G2, C phase | 500 | [7 empty] | DS1 |  | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 1 tripod failed |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 0 | Disconnect Switch DS | [8 empty] | Vertical Swing |  | Bank H | 500 | [7 empty] | DS1 |  | Qualified by a 0.5g 10 cycle sine-beat shake table test | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 0 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | Banks G1 & G2 | 500 | [7 empty] | DS1 |  | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference |  |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E22, phase B, C | 230 |  |  |  |  | Southern States |  |  | DS3 |  | Center break, sine beat tested | heavily braced support | 1 column failed, see page 56 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E2A, phase A, C | 230 | [7 empty] | DS3 |  | Center break |  | 1 column failed, see page 56 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E32, phase C | 230 | [7 empty] | DS3 |  | Center break | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E32, phase B | 230 | [7 empty] | DS3 |  | Center break |  | 1 column failed, see page 56 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E41, phase C | 230 | [7 empty] | DS3 |  | Center break | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E51, phase C, B | 230 | [7 empty] | DS3 |  | Center break | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E51 phase A | 230 | [7 empty] | DS3 |  | Center break |  | 1 column failed, see page 57 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E81 | 230 | [7 empty] | DS3 |  | Center break | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E91, phase B ,C | 230 | [7 empty] | DS3 |  | Center break |  | 2 column failed, see page 59 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E91, phase A | 230 | [7 empty] | DS3 |  | Center break |  | 1 column failed, see page 59 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E122, phase B | 230 | [7 empty] | DS3 |  | Center break |  | 1 column failed, see page 59 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged | Yes | 2 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E92, phase B, C | 230 | [7 empty] | DS3 |  | Center break |  | 2 column failed, see page 59 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 10 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Southern States |  |  | DS3 |  | Center break, sine beat tested | heavily braced support | See page 56 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 146 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  | Center break | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2010 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 17 | Circuit Switcher CS | [11 empty] | 230 | [7 empty] | CS1 |  |  |  | direct communication from Rulon Fronk |  |  |  | 2003-03-31
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester |  |  |  | Free Standing | [6 empty] | Bank H, C phase | 500 | [7 empty] | LA5 |  |  | Post Supported | Failure in porcelain |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester | [11 empty] | 500 | [7 empty] | LA5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Lightning Arrester |  |  |  | Free Standing | [6 empty] | Bank H, A phase | 500 | [7 empty] | LA5 |  |  | Post supported |  |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 5 | Lightning Arrester | [11 empty] | 500 | [7 empty] | LA5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 0 | Potential Trans. PT | [11 empty] | 230 | [7 empty] | PT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Potential Trans. PT | [11 empty] | 230 | [7 empty] | PT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 12 | Transformer TR | [11 empty] | 230 | 34.5 | [6 empty] | TR1 |  |  |  | direct communication from Rulon Fronk |  |  |  | 2003-03-31
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 0 | Transformer TR | [11 empty] | 230 | 34.5 | [6 empty] | TR1 |  |  |  | direct communication from Rulon Fronk |  |  |  | 2003-03-31
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 9 | Transformer TR | [11 empty] | 500 | 230 |  |  |  |  | 1 phase |  | TR3 |  |  |  | direct communication from Rulon Fronk |  |  |  | 2003-03-31
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 0 | Transformer TR | [11 empty] | 500 | 230 |  |  |  |  | 1 phase |  | TR3 |  |  |  | direct communication from Rulon Fronk |  |  |  | 2003-03-31
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Wave Trap WT |  |  |  |  | Vertically Suspended | [5 empty] | E32 phase A | 230 | [7 empty] | WT1 |  |  |  | failure of 1 post insulator restraint, see page 56 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Wave Trap WT |  |  |  |  | Vertically Suspended | [5 empty] | E42 phase A | 230 | [7 empty] | WT1 |  |  |  | failure of post insulator restraints, see page 57 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Wave Trap WT |  |  |  |  | Vertically Suspended | [5 empty] | E52 phase A | 230 | [7 empty] | WT1 |  |  |  | failure of post insulator restraints, see page 57 ASCE |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 8 | Wave Trap WT |  |  |  |  | Vertically Mounted | [6 empty] | 230 | [7 empty] | WT1 |  |  |  | Failure of support post insulators |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Wave Trap WT |  |  |  |  | Vertically Suspended | [5 empty] | Bank G1 & G2 | 500 | [7 empty] | WT2 |  | Post restraint | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 4 | Wave Trap WT |  |  |  |  | Vertically Mounted | [6 empty] | 230 | [7 empty] | WT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from OFR 94-141, Feb. 1994, USGS, fault plane solution from report OSMS 94-07, damage data from PGE report 005-96.23, Matsuda et al. & ASCE Monograph 8 "Northridge Eq. Lifeline Performance & Post Eq Response" Ed. by A. Schiff , Spectra Recon. Report 95-03 pp189-212 |  | SS#34 | LADWP | Transmission SS | [6 empty] | 0.595 | 1 | 1.424 | 1.615 | Yes | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Wave Trap WT |  |  |  |  | Vertically Suspended | [5 empty] | Bank H | 500 | [7 empty] | WT2 |  | Cable restraint | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 0 | Circuit Breaker CB | Bulk Oil | [10 empty] | 230 | [7 empty] | CB20A | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 114 | Circuit Breaker CB | Bulk Oil | [10 empty] | 230 | [7 empty] | CB20A | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 0 | Current-Voltage Transformer | [11 empty] | 230 | [7 empty] | CC1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 27 | Current-Voltage Transformer | [11 empty] | 230 | [7 empty] | CC1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Circuit Switcher CS | [11 empty] | 500 | [7 empty] | CS2 |  |  |  | Post insulators failed, base bolts stretched |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Circuit Switcher CS | [11 empty] | 500 | [7 empty] | CS2 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [11 empty] | 230 | [7 empty] | DS2 |  |  |  | Post insulator failed |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 119 | Disconnect Switch DS | [11 empty] | 230 | [7 empty] | DS2 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Disconnect Switch DS | [11 empty] | 500 | [7 empty] | DS1 |  |  |  | Post insulators failed |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 4 | Disconnect Switch DS | [11 empty] | 500 | [7 empty] | DS1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Lightning Arrester |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 18 | Lightning Arrester |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Lightning Arrester |  |  |  | Post-supported | [7 empty] | 500 | [7 empty] | LA5 |  |  |  | Failed at based of column |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 0 | Lightning Arrester |  |  |  | Post-supported | [7 empty] | 500 | [7 empty] | LA5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Potential Trans. PT | [11 empty] | 230 | [7 empty] | PT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Potential Trans. PT | [11 empty] | 230 | [7 empty] | PT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Potential Trans. PT | [11 empty] | 500 | [7 empty] | PT5 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Transformer TR | [11 empty] | 230 | 34.5 | [6 empty] | TR2 |  | 3 phase |  | Lost LAs |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 5 | Transformer TR | [11 empty] | 230 | 34.5 | [6 empty] | TR2 |  | 3 phase | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 0 | Transformer TR | [11 empty] | 500 | 230 | [6 empty] | TR3 |  | single phase | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Transformer TR | [11 empty] | 500 | 230 | [6 empty] | TR3 |  | single phase | [5 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 0 | Wave Trap WT |  |  |  |  | Suspended | [6 empty] | 500 | [7 empty] | WT2 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Wave Trap WT |  |  |  |  | Suspended | [6 empty] | 500 | [7 empty] | WT2 |  |  |  | All wave traps undamaged but restraint on one WT damaged |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Wave Trap WT |  |  |  |  | Supported on DS frame | [6 empty] | 230 | [7 empty] | WT1 |  |  |  | Post failed |  |  |  | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 4 | Wave Trap WT |  |  |  |  | Supported on DS frame | [6 empty] | 230 | [7 empty] | WT1 | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 0 | Pothead | [11 empty] | 230 | [7 empty] | PH | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#35 | LADWP | Transmission SS | [6 empty] | 0.453 | 0.876 | 0.859 | 1.293 | Yes | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 9 | Pothead | [11 empty] | 230 | [7 empty] | PH | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 72 | Circuit Breaker CB | Bulk Oil | [10 empty] | 230 | [7 empty] | CB20A |  |  | Most units are anchored with bolts through skid frame. | Some units showed signs of distress in the anchore bolts, that is, chipped paint or bent bolts. |  |  | 339 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 8 | Coupling Voltage Trans. CVT | [5 empty] | on structure with WT | [5 empty] | 230 | [7 empty] | CC1 |  | Total number of CCVTs disagrees with number in TCLEE report page 61 | Note that these units are supported on a beam spanning 2 DS rather than on its own support sturcture. |  |  |  | 343 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 14 | Coupling Voltage Trans. CVT | [11 empty] | 230 | [7 empty] | CC1 | [6 empty] | 344 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Coupling Voltage Trans. CVT | [11 empty] | 230 | [7 empty] | CC1 | [6 empty] | 345 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Potential Transformer PT | [11 empty] | 230 | [7 empty] | PT1 | [7 empty] | 2002-07-21
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E1, Aphase | 230 | [7 empty] | DS2 |  | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. |  | Both support columns failed. |  |  | 337 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 4 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E1, A, B, C phase | 230 | [7 empty] | DS2 |  | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | Note that a rigid bus connects the Bus 1 and Bus 2 Positions. | All of these failures were to the column that is connected by rigid bus to the adjacent switch. Note that these switches are braced in the direction of the rigid bus connection. |  |  | 338 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  | E1, C phase | 230 | [7 empty] | DS2 |  | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. |  | Both support columns failed |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 12 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS2 |  | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. |  | unknown failure mode |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 54 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS2 |  | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. |  | Some of these units have been damaged, but their position is not known. |  |  | 336 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Lightning Arrester LA |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 |  | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | 2 LA failed at standoff |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Lightning Arrester LA |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 |  | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | 1 failed at base of LA. |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Lightning Arrester LA |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 |  | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All LA failed but it is not known if there are standoffs. |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Lightning Arrester LA |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 |  | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All LA failed but it is not known if there are standoffs. |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Lightning Arrester LA |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 |  | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. |  |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Small Rad | [8 empty] | Bank A | 230 | 34.5 |  |  |  |  | 3-phase |  | TR2 |  | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | All high voltage bushings moved. 2 LA failed at standoff, 1 at base of LA. |  |  | 349 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Small Rad | [8 empty] | Bank B | 230 | 34.5 |  |  |  |  | 3-phase |  | TR2 |  | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All high voltage bushings moved. Also leaks in low voltage bushings. All LA failed but it is not known if there are standoffs. Anchor bolts stretched. There was a oil leak but it is not known if it is just the bushings. |  |  | 350 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Small Rad | [8 empty] | Bank D | 230 | 34.5 |  |  |  |  | 3-phase |  | TR2 |  | Schematic on page 66 of ASCE | LA bus connections not to bushings. | All high voltage bushings moved. 1 LA failed at standoff, 2 at base of LA. |  |  | 352 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Small Rad | [8 empty] | Bank C | 230 | 34.5 |  |  |  |  | 3-phase |  | TR2 |  | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | It is not known if there are standoffs. |  |  | 351 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Wave Trap WT |  |  |  |  | V. Dual Post | [6 empty] | 230 | [7 empty] | WT1 |  |  | Note that this unit had the post insulators supported on a beam spanning 2 DS | Unit was tilting, but was functional. |  |  | 346 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  |  | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | Unit had to be removed and replaced, but damage not known. |  |  | 347 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  |  | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | Units tilted,but functional. |  |  | 348 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Wave Trap WT |  |  |  |  | V. Dual Post | [6 empty] | 230 | [7 empty] | WT1 |  |  | Note that this unit had the post insulators supported on a beam spanning 2 DS |  |  |  | 340 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  |  | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. |  |  |  | 341 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#36 | LADWP | Transmission SS | 18821 Parthenia | [5 empty] | 0.4284 | 0.7105 | 0.9994 | 1.0029 | No | Tertiary formation - soft rock |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 2 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  |  | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. |  |  |  | 342 | 1998-05-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#37 | LADWP | Transmission SS | [10 empty] | No | [7 empty] | Damaged |  | 6 | Lightning Arrester LA |  |  |  | TR Boom Mounted | [7 empty] | 230 | [7 empty] | LA1 |  |  |  | 2 at standoff , 4 at arrester |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#37 | LADWP | Transmission SS | [10 empty] | No | [7 empty] | Undamaged |  | 3 | Lightning Arrester LA |  |  |  | Post mounted | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#37 | LADWP | Transmission SS | [10 empty] | No | [7 empty] | Damaged |  | 2 | Transformer TR | [11 empty] | 230 | 34.5 |  |  |  |  | 3-phase |  | TR2 |  |  |  | 6 Leaking 230 kVbushings, 6 LA failed |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#37 | LADWP | Transmission SS | [10 empty] | No | [7 empty] | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | 34.5 |  |  |  |  | 3-phase |  | TR2 | [7 empty] | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6000 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 54 | Circuit Breaker CB | Bulk Oil | [10 empty] | 230 | [7 empty] | CB20A | [6 empty] | 368 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6001 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Potential Transformer PT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | PT1 |  |  | There may be a slack problem in that there is a short flexible connection to a rigid bus that is supported by disconnect switch structures. Pot head support structure is also connected to the rigid bus. |  |  |  | 361 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6002 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 15 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | CC1 | [6 empty] | 360 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6002 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | CC1 | [7 empty] | 2002-07-11
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6003 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 33 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  | 1600 | 900 |  | ITE | Type DR-5 |  | DS3 |  |  |  | These units had deformed operating mechanism that prevented their operation. None of the post insulators were damaged. | It took 2 days to identify the problem and the fix and 2 hour for each (3 phases) to make repairs after that. |  | 353 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6004 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 24 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  | 1600 | 900 |  | ITE | Type DR-5 |  | DS3 |  |  |  | These units had deformed operating mechanisms that prevented their operation. None of the post insulators were damaged. | It took 2 days to identify the problem and the fix and 2 hour for each (3 phases) to make repairs after that. |  | 369 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6005 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 6 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  |  |  | unknown damage | Post insulators used for bus supports in PE4,5,6 were canibalized to reconstruct DS. |  | 354 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6006 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 6 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  |  | rigid bus connection | One of the columns failed. 10 were adjacent to CB and were provided with good slack so that inertial loads were probably the cause of failure. One unit was connected to a bus with an intermediate drop and bus dynamics may have contributed to failure | Post insulators used for bus supports in PE4,5,6 were canibalized to reconstruct DS. |  | 355 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6006 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 13 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  |  | rigid bus connection | Both columns failed. Interaction between columns may have contributed to the dual failures. . |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6007 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 23 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 | [7 empty] | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6007 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 5 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | 1 column failed |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6007 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | both columns failed |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6007 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 4 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 | [7 empty] | DS3 |  |  | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS |  |  |  |  | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6008 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 6 | Lightning Arrester LA |  |  |  | Frame | [6 empty] | TR Bank B & C | 230 | [7 empty] | LA1 |  |  | Standoffs failed | Standoffs failed |  |  | 364 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6009 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 2 | Lightning Arrester LA |  |  |  | Frame- Pothead | [7 empty] | 230 | [7 empty] | LA1 |  |  | Unusual installation in that frame is much lower than that used for TRs. LA are on standoffs. There is marginal slack to a rigid bus that is supported on disconnect switches. | Standoffs failed |  |  | 365 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6010 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Lightning Arrester LA |  |  |  | TR Boom Mount | [6 empty] | TR Bank E | 230 | [7 empty] | LA1 |  |  | No Standoffs | Failed at base of LA |  |  | 367 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6011 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 3 | Lightning Arrester LA |  |  |  | Free Standing | [6 empty] | TR Bank A | 230 | [7 empty] | LA1 | [6 empty] | 363 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6012 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 7 | Lightning Arrester LA |  |  |  | Frame- Pothead | [7 empty] | 230 | [7 empty] | LA1 |  |  | Unusual installation in that frame is much lower than that used for TRs. LA are on standoffs. There is marginal slack to a rigid bus that is supported on disconnect switches. |  |  |  | 366 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6013 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Separate Rad | [8 empty] | Bank B | 230 | 34.5 | [6 empty] | TR1 |  | TR in accountic enclosure. Separately supported radiators. Conservator tank with 2 supports. LA supported on frame with standoffs. | Ao and Co LA drops from bus, Bo from bushing. see page 71 ASCE | Bo Bushing has damaged bus stud. All LA failed, A & C at standoffs and B at LA base. Conservator stretched bolts and shifted in slotted connections, strain piping and lost all 1000g oil. |  |  | 357 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6014 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Separate Rad | [8 empty] | Bank C | 230 | 34.5 | [6 empty] | TR1 |  | TR in accountic enclosure. Separately supported radiators. Conservator on 2 supports above TR. LA supported on frame. . | All LA have bus drops from bus. | All failed at standoffs and were not damaged. Signs of oil leak (spray on conservator) but source could not be found. |  |  | 358 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6015 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Separate Rad | [8 empty] | Bank A | 230 | 34.5 | [6 empty] | TR1 |  | TR in accountic enclosure. Separately supported radiators, which were moderately large. Conservator on top of radiators. LA supported on independent posts without standoffs. | LA drops from bus. | Signs of oil leak at valve inside of enclosure, but it looks old. |  |  | 356 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6016 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Small Rad | [8 empty] | Bank E | 230 | 138 | [6 empty] | TR1 |  | LA on boom without standoffs. High voltage LA have drops from bus. see page 71 ASCE | Unit anchored with gusseted angle to pull tabs. | 230 KV LA failed. They were boom mounted without standoffs. Small radiators. Flexible end anchors to pull tabs contributed to failure of bolted angles along side. |  |  | 359 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6017 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 3 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  |  | These units have marginal slack. | 1 WT w/ failed posts at lower sand ring, 2 failed welds at top of posts connecting to wave trap support channel. | Two units were restored by bolting angles between channel and post cap. |  | 362 | 1998-05-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6018 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 | [6 empty] | 370 | 1998-06-10
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07,damage from ASCE Monograph 8 "Northridge Eq, Lifeline Performance & Post-Eq Response", 1995 Ed. by Schiff |  | SS#38 | LADWP | Transmission SS | 6019 Wilbur | [5 empty] | 0.3669 | 0.6383 | 0.9208 | 0.8779 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 9 | Pothead | [11 empty] | 230 | [15 empty] | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#41 | SCE | Transmission SS | [6 empty] | 0.5567 | 0.7911 | 1.0901 | 1.2833 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Disconnect Switch DS | [8 empty] | Horizontal - Low Design |  |  | 230 | [7 empty] | DS3 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#41 | SCE | Transmission SS | [6 empty] | 0.5567 | 0.7911 | 1.0901 | 1.2833 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 6 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 230 | [7 empty] | LA1 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#41 | SCE | Transmission SS | [6 empty] | 0.5567 | 0.7911 | 1.0901 | 1.2833 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Damaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | three phase |  | TR2 |  |  |  | radiator leak |  |  |  | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#41 | SCE | Transmission SS | [6 empty] | 0.5567 | 0.7911 | 1.0901 | 1.2833 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville |  |  |  |  | Undamaged |  | 1 | Transformer TR | [11 empty] | 230 | 66 |  |  |  |  | three phase |  | TR2 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 1995 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 12 | Circuit Breaker CB | Dead Tank | [10 empty] | 230 |  |  |  |  | Westinghous-Mitsubishi Power Breaker | 200-SFMT-63B |  | CB20 |  |  | Has very good slack to DSs. Pict 1-35 | E91 A had a loose bolt at south east corner. |  |  | 320 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 1996 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 45 | Circuit Breaker CB | Bulk Oil | [10 empty] | 230 |  |  |  |  | Siemens-Allis & ITE |  | 1983 & 1971 | CB20A | [7 empty] | 2002-06-17
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 1997 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 2 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | GE | 4CD3 |  | CC1 | 675 | Installed on 6-3/4" diameter 8'-6" tall | Good slack in bus connection | A failed at lower sand ring and B did not look damaged on original trip. Unit was removed and porcelain was fractured 1/3 of the way up from base. Ao is would be inertial loads. Pict 3-34, 28-36 |  |  | 319 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 1998 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 1 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | GE |  |  | CC1 |  |  | Units are on pedestals 6-3/4" diameter and 8'-6" tall | This unit was found removed 3/15/94. Pict 28-34 |  |  | 332 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 1999 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 8 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | GE | 4CD3... |  | CC1 | 675 | Units are on pedestals 6-3/4" diameter and 8'-6" tall | Good slack in bus connection. Pict 2-15 |  |  |  | 317 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2000 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 10 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | GE | 4CD3... |  | CC1 | 675 | Supported on 6-3/4" 8'-6" tall | Good slack in bus connection. Pict 24-8 |  |  |  | 318 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2001 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 2 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | CC1 |  | A is Nisson Denki, B & C are GE. Pict. 24-4 | A & C have Bellville washers, B does not? |  |  |  | 315 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2002 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 6 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | Haeffey |  |  | CC1 |  | mounted on 12" diameter post that is 7' high. Can is sealed in unusual way. Support post has 8 large gussets at base and top. Pict. 1-30, 28, 26, 25, 28-23, 22, 21 |  |  |  |  | 316 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2003 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 4 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | Westinghouse |  |  | CC1 |  | Units have bellville washers. Support column is 13" diameter and 7'-8" tall. pict 28-27 |  |  |  |  | 333 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2004 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 3 | Coupling Voltage Trans. CVT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | Trench |  |  | CC1 |  | Support column is 13" diameter and 7'-8" tall all connected to a large metal base. Pict 28-34 |  |  |  |  | 334 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2005 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 4 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Southern States |  |  | DS3 |  | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. |  | Support shaft failed so that it looked like a fatigue failure. Similar failure at RS E. Orientation of fractures are not consistant with position of arm. 92CL Pict 1-29,28,27,26,25. 101BL Pict1-21,20. 101BB Pict1-18,17,16,15. 91AB Pict 1-14. 28-24. Bus |  |  | 312 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2006 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Southern States |  |  | DS3 |  | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. |  | Porcelain failure at base. Fracture surface (hinge) suggests that it failed due to a pull by the bus. There were two failures adjacent to line drop. Pict 1-24,23,22,12,11. 28-24. Bus drop 1-34 indicated that swing at top of drop may have lifted drop. |  |  | 313 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2007 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 15 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  | Units supported on two columns |  | All failed at the base of the porcelain. Only one column failed. column E82CLB, E82ALB, E83Ab1b1, E83Ab2b1, E81CLL, E72BLL, E7Cb2b2, E73Bb2b2, E73Ab2b1, E71CBL, E71ALB, Bank F 230 Bank, Bank F 230 Bbank, Bank F 220 BB, Pict 1-8, 1-7,2-37, 2-18 |  |  | 322 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2008 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 3 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  | Units supported on two columns |  | Post insulators failed at sand ring. Both insulators failed. Pict 1-8 |  |  | 323 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2009 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  | Units supported on two columns. Pict 28-32, 31 |  | Post insulators failed at sand ring. |  |  | 335 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2010 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 18 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Southern States |  |  | DS3 |  | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. Pict 1-36 |  |  |  |  | 311 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2010 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 1 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Southern States |  |  | DS3 |  | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. | [5 empty] | 2002-07-19
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2011 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 83 | Disconnect Switch DS | [8 empty] | Horizontal Swing |  |  | 230 |  |  |  |  | Cole |  |  | DS3 |  | Units supported on two columns. 8-1/2" x 5" with about 3/8" wall with long direction in line with closed arm. Pict 28-31 |  |  |  |  | 321 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2012 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 12 | Lightning Arrester LA |  |  |  | TR Boom Mount | [7 empty] | 230 | [7 empty] | LA1 |  | Pict 28-32, 2-13 | on porcelain standoffs, Support plates look thin. |  |  |  | 329 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2013 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 4 | Potential Trans. PT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | PT1 |  | Support post is 6-3/4"diameter and 7'-10" high. Pict 3-38, 37,36,35,,33,32. | Units had Bellville washers. The base has small gussets. | Units all failed at the sand ring at base, except 230 Bus 2 A where damage was not obvious, but must have been it cracked. It did not have oil spill below it. Note that bus 2 side anchore bolts were streched and one was loose. On Bus 1 A & C o had st |  |  | 310 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2014 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 6 | Potential Trans. PT | [5 empty] | Post Mounted | [5 empty] | 230 |  |  |  |  | Westinghouse |  |  | PT1 |  | Support columns is very large with gussets at top but not at base. Support column is 15" Square and 7'-4" tall from top of lower support to bottom of top support. Pict. 1-37,15 | Units did not have Bellville washers. |  |  |  | 309 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2015 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 2 | Potential Trans. PT | [5 empty] | Post Mounted | [5 empty] | 230 | [7 empty] | PT1 |  | These units have much smaller section support column that 220 KV bus. Support post is 6-3/4"diameter and 7'-10" high. | Units had Bellville washers | Note that bus 2 side anchore bolts were streched and one was loose. On Bus 1 A & C o had streched bolts but were undamaged. Phase B did not strech but failed. Phase C gussett at base showed signs of distress. Pict 3-33 |  |  | 314 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2016 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 1 | Transformer TR |  | Small Rad | [8 empty] | Bank F | 230 | 220 |  |  |  | Westinghouse |  |  | TR2 | 537000 | 3 phase Auto transformer 220 to 230 KV | Radiators braced at the bottom | Weld to embedment failed. It was a poor weld and not much material was put down. The concrete was fractured where the embedment tried to pull out. The transformer moved about 14" to the north. Pict 2-10,, 9, 8, 7, 6, 28-32 |  |  | 331 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2017 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 1 | Transformer TR |  | Small Rad | [8 empty] | Bank E | 230 | 220 |  |  |  | Westinghouse |  |  | TR2 | 527000 | 3 phase Pict 2-13 | Radiators braced at the bottom, welded to embedment |  |  |  | 330 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2018 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 1 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  |  |  | Weld on one side channel failed. Other channel tore. Pict 2-35, 34, 33, 32, 29, 2-17 |  |  | 328 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2019 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Damaged |  | 1 | Wave Trap WT |  |  |  |  | V. Suspended | [6 empty] | 230 | [7 empty] | WT1 |  | Pict 24-6 |  | bolts failed on restraint, WT ok |  |  | 324 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2020 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 2 | Wave Trap WT |  |  |  |  | V. Suspended | [6 empty] | 230 | [7 empty] | WT1 |  | Pict 24-7, 8 |  |  |  |  | 325 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2021 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 1 | Wave Trap WT |  |  |  |  | V. Post Mounted | [6 empty] | 230 | [7 empty] | WT1 |  | Units supported on three columns. Pict 24-4 |  |  |  |  | 326 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source info. from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from Northridge Eq. Lifeline Performance & Post-Eq Response, TCLEE Monograph 8, 2022 |  | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | [5 empty] | 0.6233 | 0.8683 | 1.1716 | 1.3347 | No | Quaternary formation - soil |  | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station |  |  |  |  | Undamaged |  | 2 | Wave Trap WT |  |  |  |  | H. Post-Insulator | [6 empty] | 230 | [7 empty] | WT1 |  | Pict 28-29 |  |  |  |  | 327 | 1998-04-06
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Damaged |  | 1 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | General Electric | ATB |  | CB15 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 8 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | General Electric | ATB |  | CB15 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Damaged |  | 2 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | Westinghouse | seismic |  | CB72s | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 4 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | Westinghouse | seismic |  | CB72s | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 33 | Circuit Breaker CB | Dead Tank | [10 empty] | 220 | [5 empty] | SF-6 |  | CB20 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 21 | Circuit Breaker CB | Live Tank | [10 empty] | 220 |  |  |  |  | Siemans |  |  | CB57 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 9 | Circuit Breaker CB | Live Tank | [10 empty] | 500 |  |  |  |  | Westinghouse | Puffers |  | CB73 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 6 | Circuit Breaker CB | Dead Tank | [10 empty] | 500 | [5 empty] | SF-6 |  | CB77 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Damaged |  | 2 | Current Transformer CT | [7 empty] | Low Seismic |  |  |  | 500 | [7 empty] | CT5 |  |  |  | broken |  |  |  | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 24 | Current Transformer CT | [7 empty] | Low Seismic |  |  |  | 220 | [7 empty] | CT1 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 13 | Current Transformer CT | [7 empty] | Low Seismic |  |  |  | 500 | [7 empty] | CT5 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Damaged |  | 21 | Disconnect Switch DS | [8 empty] | Low Design |  |  | 500 | [7 empty] | DS1 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 45 | Disconnect Switch DS | [8 empty] | Low Design |  |  | 500 | [7 empty] | DS1 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 108 | Disconnect Switch DS | [8 empty] | Low Design |  |  | 220 | [7 empty] | DS3 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 10 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 220 | [7 empty] | LA1 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Damaged |  | 7 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 500 | [7 empty] | LA5 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 21 | Lightning Arrester LA |  |  |  | Low Design | [7 empty] | 500 | [7 empty] | LA5 | [7 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Damaged |  | 3 | Transformer TR | [11 empty] | 500 | 230 |  |  |  |  | single phase |  | TR3 |  | composite bushing |  | radiator leaks |  |  |  | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07 |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 7 | Transformer TR | [11 empty] | 500 | 230 |  |  |  |  | single phase |  | TR3 |  | composite bushing | [5 empty] | 2002-04-03
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from ASCE TCLEE Monograph 8, "Northridge Eq., Lifeline Performance and Post-Eq Response", ed. Schiff |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 10 | Wave Trap WT | [11 empty] | 500 | [7 empty] | WT2 |  | Suspended | [5 empty] | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from ASCE TCLEE Monograph 8, "Northridge Eq., Lifeline Performance and Post-Eq Response", ed. Schiff |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Undamaged |  | 60 | Bus Support | [11 empty] | 230 | [7 empty] | BS | [7 empty] | 2002-07-09
Northridge | 1998-01-18 | 4:31 | 34.211 | 118.538 | 6.6 | 18 | Thrust | [5 empty] | Source information from open file report 94-141, February 1994, USGS, fault plane solution from report OSMS 94-07, Damage from ASCE TCLEE Monograph 8, "Northridge Eq., Lifeline Performance and Post-Eq Response", ed. Schiff |  | SS#45 | SCE | Transmission SS | [6 empty] | 0.139 | 0.2197 | 0.3318 | 0.3082 | Yes | Mesozoic formation - hard rock |  | Ground Motion from Paul Somerville, Mw=6.7 |  |  |  |  | Damaged |  | 4 | Bus Support | [11 empty] | 230 | [7 empty] | BS | [7 empty] | 2002-07-09

## Facility
EQ_NAME | FACIL_NAME | FACIL_OWN | TYPE_FACIL | FACIL_ADD | FACIL_LAT | FACIL_LONG | EPICEN_DIST | DIST_RUPT | SITE_MMI | EST__PEAK_ACC | SITE_COMMENT | GRND_MOTION | DAMAGE_PAR_1 | DAMAGE_PAR_2 | RESTORATION | IMPACT_DAMAGE | REFERENCES
2-Whittier Narrows | SS#1 | SCE | Power Plant | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.058 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#1 | SCE | Power Plant | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.058 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#2 | SCE | Transmission SS | 2nd Ave & St. Joseph | 0 | 0 | 0 | 0 | 0 | 0.163 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos | 0 | 0 | 0 | 0 | 0 | 0.079 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos | 0 | 0 | 0 | 0 | 0 | 0.079 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos | 0 | 0 | 0 | 0 | 0 | 0.079 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.101 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#11 | SCE | Transmission SS | Compton Blvd east of Avalon, Compton | 0 | 0 | 0 | 0 | 0 | 0.094 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#11 | SCE | Transmission SS | Compton Blvd east of Avalon, Compton | 0 | 0 | 0 | 0 | 0 | 0.094 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#15 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
2-Whittier Narrows | SS#33 | SCE | Transmission SS | 1371 Monterey Pass Rd | 0 | 0 | 0 | 0 | 0 | 0.171 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Coalinga | SS#12 | PG&E | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2985 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Coalinga,CA, EQ of May 2, 1983, EERI Report 84-03, Jan. 1984 2. CDMG OSMS 83-5.2 3. PG&E, Coalinga EQ of May 2, 1983, Field Inspection Report (unbound), July 20, 1983
Landers | SS#5 | SCE | Generating Station | Daggett | 0 | 0 | 0 | 0 | 0 | 0.352 | 0 | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra | 0 | 0 | 0 | 0 | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq.
Landers | SS#5 | SCE | Generating Station | Daggett | 0 | 0 | 0 | 0 | 0 | 0.352 | 0 | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra | 0 | 0 | 0 | 0 | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq.
Landers | SS#5 | SCE | Generating Station | Daggett | 0 | 0 | 0 | 0 | 0 | 0.352 | 0 | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra | 0 | 0 | 0 | 0 | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq.
Landers | SS#5 | SCE | Generating Station | Daggett | 0 | 0 | 0 | 0 | 0 | 0.352 | 0 | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra | 0 | 0 | 0 | 0 | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq.
Landers | SS#5 | SCE | Generating Station | Daggett | 0 | 0 | 0 | 0 | 0 | 0.352 | 0 | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra | 0 | 0 | 0 | 0 | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq.
Landers | SS#5 | SCE | Generating Station | Daggett | 0 | 0 | 0 | 0 | 0 | 0.352 | 0 | ground motion from Paul Somerville, Mw=7.3, Ref 1 has records and spectra | 0 | 0 | 0 | 0 | 1. EPRI TR-103454 June 24 1992 Landers & Big Bear Eq.
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#25 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2366 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI NP-7500-SL 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#26 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2807 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to V. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#28 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.2064 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Loma Prieta | SS#39 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1858 | 0 | ground motion from Paul Somerville, Mw=7.0 | 0.2 | 0 | 0 | 0 | 1. Earthquake Spectra, Supplement to Vo. 6, L.P Recon. Report, May 1990, 2. USGS Open File Report 89-568 3. USGS Open-File Report 90-247, April 90 4. CDMG OSMS 89-06 5. EPRI 6. EPRI draft aftershock report from URS
Morgan Hill | SS#20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days which CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days which CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | 0 | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | 0 | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | Damaged CB caused one of the 2 Pacific Interties to open and stay open. One of the PIs was open for 3 days while CB was repaired. There was no impact (other than reliability) as the remainng PI could carry the load. | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | 0 | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | 0 | 0 | 0
Morgan Hill | SS#21 | PG&E | Transmission SS | 0 | 0 | 0 | 25 | 0 | 0 | 0.06 | 0 | Water type waves were seen approaching the site from the north northwest. From under the desk, the motion was wave-like. This description suggests a periodic type motion which may have a larger impact on equipment with a frequency near the input motion | 0.06 | 0 | 0 | 0 | 0
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
Morgan Hill | SS#24 | PG&E | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol 1, No. 3, May 1985 2. CDMG OSMS 85-04 3. EPRI ?
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
North Palm Springs | SS#7 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.836 | 0 | Ground motion from EPRI NP-5607 | 0.55 | 0 | 0 | 0 | 1. CDMG OSMS-86-05 2. CDMG OSMS 87-01 3. USGS OFR 87-155 4. SCE Lessons Learned from July 8, 1986 Palm Springs EQ, P S EQ Task Force, Dec. 1986 5. LADWP EQ Damage Assessment Report of SCE's Devers Bulk Power Station 7/17/86 6. EPRI NP-5607 1/88
Pt. Mugu | SS#40 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1158 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Pt. Mugu | SS#40 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1158 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Pt. Mugu | SS#40 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1158 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Pt. Mugu | SS#40 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1158 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
San Fernando | SS#1 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#1 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#1 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#1 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#1 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#1 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#1 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0 | ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#18 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#18 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#18 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#18 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#18 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#18 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | Ground motion from Paul Somerville, Mw=6.6 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#19 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.097 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | Misc | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | Misc | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | Misc | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.536 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#44 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71
San Fernando | SS#44 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71
San Fernando | SS#44 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71
San Fernando | SS#44 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71
San Fernando | SS#44 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
San Fernando | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. San Fernando CA EQ of 2/9/71, US Dept of Commerce, NOAA, V3, Wash, DC, 1973 2. San Fernando EQ 2/971, Effects of Power System Operations & Facilities, LADWP, 10/74 3. EQ of 2/971 Effects on Power Sys Fac, Analysis Present Aseismic..., LADWP, 6/71
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Santa Barbara | SS#13 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0.28 | 0 | 0 | 0 | 1. Processed Data from the SM Records of the Santa barbra EQ of 13 August 1978, Final . . Results, CDMG, Special Report 144, Vol 1 (2 &3)
Sierra Madre | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sierra Madre | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sierra Madre | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sierra Madre | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sierra Madre | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sierra Madre | SS#14 | SCE | Transmission SS | Foothill Fwy & Foothill Blvd, Pasadena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Tejon Ranch | SS#9 | CDWR | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | Switchyard associated with pump plant is several hundred yards north of pump plant and is situated on fill that spans a ravine. Most of damage was onwest end of site where fill was relatively thin. Transformers were located | SM instrument located in the basement of the pump plant recorded a .08g peak horizontal acceleration. Because of the reduction due to embedment of the plant the switchyard acceleration is assumed to be 0.1g. | 0.1 | 0 | For the purposed of this report the CBs are numbered from W to E 1 to 6 and the phases A to C. CB 3 was 3000 amp unit and fed other CBs. Its failure de-energized the entire yard and plant. It took 4 days to make repairs to partially restore service. | The aqueduct was shut down for 4 days until the switchyard was partially repaired. There is 14 days of water storage below this segment of the aqueduct | 1. Lifeline Response to the Tejon Ranch EQ, Earthquake Spectra, Vol. 5, No. 4, 1989, pp791-812
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#1 | SCE | Power Station | 0 | 0 | 0 | 0 | 0 | 0 | 0.086 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#4 | SCE | Transmission SS | Norwalk, Firestone Blvd and I605 | 0 | 0 | 0 | 0 | 0 | 0.198 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#6 | SCE | Transmission SS | Cerritos, south of 605 and 91 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#8 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#10 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#15 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.186 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#15 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.186 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#15 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.186 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#15 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.186 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#16 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#17 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#19 | SCE | Transmission SS | Long Beach | 0 | 0 | 0 | 0 | 0 | 0.259 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#22 | SCE | Transmission SS | Chandler Blvd & Cordova, Burbank | 0 | 0 | 0 | 0 | 0 | 0.111 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#23 | SCE | Transmission SS | Rosemead | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#27 | SCE | Transmission SS | 13300 Mulberry Av, Whittier | 0 | 0 | 0 | 0 | 0 | 0.226 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#29 | SCE | Transmission SS | 1315 S Garfield Av, Monterey Park | 0 | 0 | 0 | 0 | 0 | 0.414 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#30 | SCE | Transmission SS | La Habra | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#30 | SCE | Transmission SS | La Habra | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#30 | SCE | Transmission SS | La Habra | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#30 | SCE | Transmission SS | La Habra | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#30 | SCE | Transmission SS | La Habra | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#30 | SCE | Transmission SS | La Habra | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#30 | SCE | Transmission SS | La Habra | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | PGA from EPRI NP-7126 | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open file report 88-357 4. EPRI NP-7126 The Oct 1, 1987 Whittier Eq: Effects on Selected Power, Indus and Comm Facilites
Whittier Narrows | SS#32 | SCE | Transmission SS | 12300 Florence Av, Santa fe Springs | 0 | 0 | 0 | 0 | 0 | 0.202 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#32 | SCE | Transmission SS | 12300 Florence Av, Santa fe Springs | 0 | 0 | 0 | 0 | 0 | 0.202 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#42 | SCE | Transmission SS | 8320 Rex Rd, Pico Rivers | 0 | 0 | 0 | 0 | 0 | 0.235 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#43 | SCE | Transmission SS | 11523 Paramount Blvd, Downey | 0 | 0 | 0 | 0 | 0 | 0.211 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#46 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.232 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#46 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.232 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#46 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.232 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#46 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.232 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#46 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.232 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Whittier Narrows | SS#46 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.232 | 0 | Ground motion from Paul Somerville | 0 | 0 | 0 | 0 | 1. Earthquake Spectra, Vol. 4, No. 1, 1988, pp 1, 43 2. CDMG Reports OSMS 87-03 and OSMS 87-05. 3. USGS open0file report 88-357
Northridge | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.2844 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.2844 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.2844 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.2844 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.2844 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#3 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.2844 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#31 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | PGA from Earthquake Spectra 95-03, April 1995 | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#34 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.595 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#35 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.453 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#36 | LADWP | Transmission SS | 18821 Parthenia | 0 | 0 | 0 | 0 | 0 | 0.4284 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#37 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northridge | SS#37 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northridge | SS#37 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northridge | SS#37 | LADWP | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6000 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6001 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6002 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6002 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6003 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6004 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6005 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6006 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6006 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6007 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6007 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6007 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6007 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6008 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6009 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6010 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6011 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6012 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6013 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6014 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6015 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6016 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6017 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6018 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#38 | LADWP | Transmission SS | 6019 Wilbur | 0 | 0 | 0 | 0 | 0 | 0.3669 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.5567 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.5567 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.5567 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#41 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.5567 | 0 | Ground Motion from Paul Somerville | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#44 | LADWP | Transmission SS | 13333 N Sepulveda Blvd | 0 | 0 | 0 | 0 | 0 | 0.6233 | 0 | Ground Motion from Paul Somerville, recording close by at the Sylmar Converter Station | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0
Northridge | SS#45 | SCE | Transmission SS | 0 | 0 | 0 | 0 | 0 | 0 | 0.139 | 0 | Ground Motion from Paul Somerville, Mw=6.7 | 0 | 0 | 0 | 0 | 0

## Equipment
FACIL_NAME | EQP_STATUS | NO_ITEMS | TYPE_EQP | PGE_CLASS | CB_SUBCLAS | TR_SUBCLAS | LA_SUBCLAS | WT_SUBCLAS | CVT_SUBCLAS | PT_SUBCLAS | CT_SUBCLAS | DS_SUBCLAS | MODS_SUBCL | DISPATCH_D | OPERATING_V | SECONDARY_V | CURRENT_RATE | BIL | MANUFACTUR | MODEL_DES | YEAR_MANUF | EQP_COMMENT | EQP_INSTAL | EQP_DAMAGE | RESTORATION | SOIL_TYPE | WEIGHT | SM_RECORD | CANTILEVER | REC_NO | REC_DATE | DAMAGE_PAR | FAIL_MODE | CONTRIBUTI
SS#1 | Damaged | 1 | Circuit Breaker CB | CB | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF6 | 0 | 0 | 0 | SF6 leaking at entrance bushing on non-CT column. Is this support column or bushing? What type of equipment. | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#1 | Undamaged | 2* | Circuit Breaker CB | CB | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | What type of equipment | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 233 | 1991-12-08 | 0 | 0 | 0
SS#2 | Damaged | 0 | Transformer TR | TR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | What was problem? | 0 | Quaternary formation - soil | 0 | No | 0 | 220 | 1991-12-08 | 0 | 0 | 0
SS#4 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | Cracked non-CT support column. | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#4 | Undamaged | 2* | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#4 | Undamaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#4 | Damaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | 3o D572975 | 0 | 0 | 0 | Oil leak. Where? Which unit? | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#4 | Damaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | Pennsylvania | 3 phase | 0 | 0 | 0 | Gas leak in man hole cover. Which unit? | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Damaged | 3 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | Blown seals on bushing #2. What is bushing #2. This is probably inner interrupter head bushing. what phases? | restored 10/5/87 @ 2300 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Undamaged | 18 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | There is also another ATB 4 or 6 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Undamaged | 9 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | 0 | 0 | 0 | 0 | This data added to reflect total of 30 at site | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1999-04-12 | 0 | 0 | 0
SS#8 | Damaged | 1 | Lightning Arrester LA | LA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Failed porcelain. How was it mounted. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#8 | Undamaged | 2 | Lightning Arrester LA | LA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How was it mounted. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#8 | Undamaged | 1 | Transformer TR | TR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | Equipment info not provided | 0 | Top plate gasket leaking. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#11 | Damaged | 1 | Current Trans. CT | CT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Oil leak | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#11 | Damaged | 0 | Transformer TR | TR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Chipped bushings. Need details. | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#15 | Damaged | 1 | Circuit Breaker CB | CB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | Voltage and type not known | 0 | What was problem? | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#33 | Damaged | 1 | Circuit Breaker CB | CB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Burnt. Is this contacts? | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#12 | Damaged | 1 | Circuit Breaker CB | CB15A | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552 C phase | 500 | 0 | 3000 | 0 | General Electric | ATB-550-2 SN 0139A8759-204 | 1971 | 0.2 g static seismic specification | 0 | Gasket leak at base of top porelain member above CT lead. | 2 days to repair. No effect on service. | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#12 | Undamaged | 8 | Circuit Breaker CB | CB15A | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552, 652 | 500 | 0 | 3000 | 0 | General Electric | ATB-550-2 | 1971 | 0.2 g static seismic specification | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#12 | Undamaged | 33 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | Oil | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#12 | Undamaged | 3 | Circuit Breaker CB | CB74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | unknown | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#12 | Undamaged | 3 | Circuit Breaker CB | CB74 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Westinghouse | ? 2 head, | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#12 | Damaged | 1 | Lightning Arrester LA | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | Bank 11B | 500 | 0 | 0 | 0 | 0 | 0 | 1972 | 0 | Installation not verified. Associated with 500/230 kV TR Bank 11. | Failed porcelain | replaced | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#12 | Undamaged | 3 | Lightning Arrester LA | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 1972 | 0 | Installation not verified. Associated with 500/230 kV TR. | 0 | 0 | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#12 | Undamaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 1 | 230 | 115 | 0 | 0 | Westinghouse | single phase | 1953 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1998-07-08 | 0 | 0 | 0
SS#12 | Damaged | 4 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 11 | 500 | 230 | 374 MVA each, 1122 MVA total | 1150 (High V bushing), 900 (Low V bushing) | General Electric | K 546561 thru 64, auto, ccoled by OA/FA/FOA | 1972 | 0 | 0 | all 500 kV bushings shifted 3/8". leaking oil | 20 days to repair. No effect on service. | (UBC S1) < 200 ft alluvium overlying sedimentary rock. | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#5 | Undamaged | 24 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#5 | Damaged | 6 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Low Design, Horizontal | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | out of adjustment | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#5 | Undamaged | 48 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Low Design, Horizontal | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#5 | Undamaged | 15 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#5 | Undamaged | 1 | Transformer TR | TR2 | 0 | Smallrad/man | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 13.8 | 0 | 0 | 0 | three phase, step up | 0 | 0 | 0 | radiator leak | fixed using wrench to tighten bolts | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#5 | Undamaged | 4 | Transformer TR | TR2 | 0 | Smallrad/man | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 13.8 | 0 | 0 | 0 | three phase, step up | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#24 | Undamaged | 15 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 3000 | 0 | Westinghouse | 3200y SF15000/20000 sn2-62y1128 | 1966 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 32000 | No | 0 | 0 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 24 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382, 222, 242, 262, 212, 312, 232, 252 | 230 | 0 | 0 | 0 | 0 | Oil | 1966 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992 Cphase | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, flexible loop bus connection to CT | All three interrupter head support columns failed. Adjacent CT and DSW did not fail. Support structure moved from under friction clips North about 1 foot. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 51 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822 B phase | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Center interrupter head support column failed. Entire column failed. Adjacent CT and DSW did not fail. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 B phase | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Interrupter head support column near disconnect switch failed. Upper part of column failed. Adjacent CT and DSW did not fail. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822 A phase | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Interrupter head support column near disconnect switch failed. Upper part of column failed. Entire column near CT failed. Adjacent CT and DSW did not fail. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922 A phase | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit tipped over, flexible loop bus connection to CT. | All interrupter head support columns failed. Entire column near CT failed. Adjacent CT did not fail. Adjacent DSW did fail. Support structure moved about 6" from under friction clips. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 A phase | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | Interrupter head support column near disconnect switch failed. The entire column failed. Adjacent CT and DSW did not fail. No significant displacement of support structure. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822 A phase | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | All interrupter head support columns failed. The entire column failed. Adjacent CT and DSW did not fail. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 2 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922 B & 722 C | 500 | 0 | 3000 | 0 | Westinghouse | SF6, Seismic, modified 1973 | 1966 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 3 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 230 | 0 | 0 | 0 | 0 | Unknown | 0 | it is unclear from documentation of this is a bulk oil or SF6 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#24 | Undamaged | 3 | Circuit Breaker CB | CB77 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 500 | 0 | 3000 | 0 | High Voltage Breaker, Inc.(Hitachi/Westinghouse) | H 550-40000-3 SN 5500A2012-203 | 1987 | Bushings are attached to sand ring which is bolted to CB body, 2 cycle interrupt, shake table tested | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 81200 | No | 0 | 0 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 6 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 1600 | 0 | General Electric | ATB6 y | 1967 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 5 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Structure/WT | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 8 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | CB Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 12 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 6 | Coupling Voltage Trans. CVT | CC5 | 0 | 0 | 0 | 0 | Structure/WT | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1992-01-02 | 0 | 0 | 0
SS#24 | Undamaged | 3 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Units had flexible loops connecting CT to CB | Some of the couplings between CT and CB may have broken | required removal of contaminated ground below each leaking CT. | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 6 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Units are mounted on Tit-tat-toe chair are are relatively flexible to rotation. Units had flexible loops connecting CT to CB | Oil leaks between bushing and tank. Some of the couplings between CT and CB may have broken | required removal of contaminated ground below each leaking CT. | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 821 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Failure of outside double post and top of inner double post. Probably due to failure of adjacent CB but taken as independent failure. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 23 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 5 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus support structure, pin and cap insulators. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 303 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 30 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ground support structure, pin and cap insulators. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 302 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 8 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus support structure, pin and cap insulators. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 301 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 12 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ground support structure, pin and cap insulators | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 170 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | TR Body Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on 500/230 kV McGraw Edison TR. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | TR Body Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | mounted on 500/230 kV Westinghouse TRs. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 7 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Associated with 230/115 kV Pennsylvania TRs (Bank 1 &2). Mounted on long boom. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | TR Body Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | mounted on 500/230 kV General Electric TRs. One of these may have been damaged (see record 292) | One of these may have been damaged? | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 151 | 1991-12-22 | 0 | 0 | 0
SS#24 | Damaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse | 0 | 0 | 0 | Associated with W 500/230 kV TR | Porcelain failure, but unit fell to ground indicating bus connection failure. TR record 67. Not sure if this was 500 or 230 kV LA that failed. | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 292 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 3 | Lightning Arrester LA | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Note that the LA with the GE were composed of 4 identical sections while others had large and medium sections and a short support section. | Associated with GE 500/230 kV TRs ( at west end of site). | Unit at east end of row may have been damaged - See record 292 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Lightning Arrester LA | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Note that the LA with the GE were composed of 4 identical sections while these had large and medium sections and a short support section. | Associated with W 500/230 kV TRs and ME TR (east end of site). | Unit at east end of row may have been damaged - See record 292 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 2 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-17 | 0 | 0 | 0
SS#24 | Undamaged | 7 | Transformer TR | TR1 | 0 | Med Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 115 | 0 | 0 | Pennsylvania | Spec. 10035, sn 0-02265-5-3, | 1950 | Rad. elements supported from tank. C&C 94700, T&F 64400, 6970 g - 54300. | 230 LA on boom, 115 LA on rad. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 211400 | No | 0 | 295 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Transformer TR | TR3 | 0 | Large Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | spare | 500 | 230 | 374 MVA | 1425 (High V bushing), 750 (Low V bushing) | Westinghouse | OA, FA, FO, Core type. | 1968 | Large radiators with each element supported from a TR tank. Rad. on sides and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 4 th from east end - use as spare. 230 LA on boom. 500 LA on independent latus structure. Units 1, 2 and 4 from east end of site. Welded to embedment | 0 | put into service when McGraw Edison units has bushing leak. | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 606000 | No | 0 | 68 | 1991-12-22 | 0 | 0 | 0
SS#24 | Damaged | 1 | Transformer TR | TR3 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 11 C phase | 500 | 230 | 374 MVA | 1425 (High V bushing), 750 (Low V bushing) | McGraw Edison | Spec. 13330, sn C06503-5-7, HV bushing no. 501.LL.716 | 1968 | Large radiators with each element supported from maniford perp. to TR tank. 70" X 127" along TR. They are supported on non-penatrating pipe at bottom and penetrating pipe at top. There are horizontal braces at bottom but not consistant (one brace was | 230 LA on rad., Welded to embedment | The 500 kV bushing shifted about 1/4" and had an oil leak at the steel/porcelain interface. Bushing was bottom attachment type rather than draw out type. Were was leak, at bushing-flange or flange -tank? | The replacement bushing is 153" from flange to top and 76" from flang down. | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 490300 | No | 0 | 69 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 2 | Transformer TR | TR3 | 0 | Large Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 11 A & B | 500 | 230 | 374 MVA each | 1425 (High V bushing), 750 (Low V bushing) | Westinghouse | OA, FA, FO, Core type. | 1968 | Large radiators with each element supported from a TR tank. Rad. on sides and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 230 LA on boom. 500 LA on independent latus structure. Units 1, 2 and 4 from east end of site., Welded to embedment | Minor oil leaks on B phase. note that A phase (east unit) lost LA, original slides indicated minor leaks at radiators (see record 292) Operational | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 606000 | No | 0 | 67 | 1991-12-22 | 0 | 0 | 0
SS#24 | Damaged | 3 | Transformer TR | TR3 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 12 | 500 | 230 | 374 MVA each | 1550 (High V bushing), 900 (Low V bushing) | General Electric | OA, FA, FO, sn D577035, -6, 7, HV bushing no. 11B775, LV bushing no. 11B765 | 1968 | 2 large radiators per side with each element supported from heavy box beam perp. to TR body and with non-penatrating connection with gusset plates for vert. load. Top connection is penetratng pipe. Each 142" long. There are diagonal braces at bottom, | West end of TR row. 230 kV LA installed on rad. | Severe oil leaks at the upper flange connection of manifold to tank. Flanges were deformed and peening was required to stop leaking. Repairs were made without the need to removed radiators or manifold. | Units were out for several days? Extensive excavation to removal contaminated soil. | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 600000 | No | 0 | 0 | 1991-12-22 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Wave trap size is about 4 feet in diameter and 6 feet long | mounted on support with CVT | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 4 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Wave trap size is about 2 feet in diameter and 4 feet long | mounted on support with CVT | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-26 | 0 | 0 | 0
SS#24 | Undamaged | 6 | Wave Trap WT | WT2 | 0 | 0 | 0 | H. Post-Insulator Mount | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | mounted on support with CVT | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 21 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | Oil | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#25 | Undamaged | 3 | Circuit Breaker CB | CB78 | 3 o Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | BBC | 242PA4020 | 0 | A relatively new three phase CB was undamaged. | Welded anchorage into embedment | 0 | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 1 | Circuit Breaker CB | CB | 3 o Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | BBC | 0 | 0 | A relatively new three phase CB was undamaged. | Welded anchorage into embedment | 0 | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 3 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Hitachi | HVB242-400001 | 0 | These were associated with Capacitor banks. | These were located on a new site adjacent to and north of the 230 kV site. | 0 | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 153 | 1991-11-26 | 0 | 0 | 0
SS#25 | Damaged | 1 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Structure/WT | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on 2 legged lattice structure with WT | Porcelain failed at its base. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 2 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Structure/WT | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | number of power mounted and structure/wt not known. | Total number at site not known.(it is known that there were a minimum of three) | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Damaged | 6 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | mounted on tall frames | Bus connections to switches were misaligned. Impact on operation is not clear but EPRI report indicates that they would not operate properly. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 117 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus supported. | Bus connections to switches were misaligned. Impact on operation is not clear but I seem to call that they would not operate properly. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 168 | 1991-11-26 | 0 | 0 | 0
SS#25 | Damaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | The LA was mounted on a long extension arm off of TR bank 4 & 4A | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 4 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | The LA was mounted on a long extension arm off of TR bank 5 | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Damaged | 5 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | The LA was mounted on a long extension arm off of TR bank 4 & 4A | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Damaged | 1 | Transformer TR | TR1 | 0 | Large Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | Westinghouse | 0 | 0 | 0 | 0 | Core damage | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 1 | Transformer TR | TR1 | 0 | Large Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | McGraw Edison | 0 | 0 | 0 | this was spare. | 0 | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Damaged | 2 | Transformer TR | TR1 | 0 | Large Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | Westinghouse | 0 | 0 | 0 | Station power components were mounted on "pipe" framed structure. This may have contributed to bushing and LA damage. There was not much slack between porcelain and support structure. | Damage to tertiary 12 kV bushings to station power, | After replacement there was still problems. Lightning Arrester had to be removed. It is not clear if this impacted station operations or operation of TRs. | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 6 | Transformer TR | TR1 | 0 | Large Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 115 | 0 | 0 | Westinghouse | 0 | 0 | 0 | 0 | Damaged LA swung and chip shed on bushng or LA | After replacement there was still problems. Lightning Arrester had to be removed. It is not clear if this impacted station operations or operation of TRs. | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#25 | Undamaged | 3 | Wave Trap WT | WT1 | 0 | 0 | 0 | frame mounted | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on support with CCVT | It is unknown how many there are. There are at least three. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 0 | 1998-07-20 | 0 | 0 | 0
SS#25 | Damaged | 3 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Transfer busses above TR banks | Transfer busses were support at top of bus support structure. Transfer busses were supported by pin and cap post insulators. | On each of two structures, post insulators failed. In one case it dropped the bus across flexible bus connected to the bus support structure. In one case a bell on a bus string was damaged and was replaced. | 0 | (UBC S1) < 20 ft alluvium overlying sedimentary rock, (NEHRP C - very dense soil and soft rock 360 m/s<Vs<=760 m/s) | 0 | No | 0 | 93 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 34 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Bulk oil type CB. | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-20 | 0 | 0 | 0
SS#26 | Damaged | 2 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Bulk oil type CB. | 0 | Sheds on bushing chipped due to failure of switch above CB. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 123 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522A | 500 | 0 | 0 | 0 | Westinghouse | SF6, Seismically Strengthened 1973 | 0 | 0 | Units anchored with unwelded, single bolt friction clips. Rigid link between CB and CT. l | Failure of one support column next to CT. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722A | 500 | 0 | 0 | 0 | Westinghouse | SF6, Seismically Strengthened 1973 | 0 | 0 | Units anchored with unwelded, single bolt friction clips. Rigid link between CB and CT. | Failure of one support column next to DS. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 147 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 10 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722, 622, 522, 512 | 500 | 0 | 0 | 0 | Westinghouse | SF6, Seismically Strengthened 1973 | 0 | 0 | Units anchored with unwelded, single bolt friction clips. Nine of the 12 units had flexible links between CB and CT, three had rigid links (522). | One phase toppled from slab, others moved, did not move or did not move significantly. Details of damage to specific units were difficult to determine from pictures. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 3 | Circuit Breaker CB | CB77 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 500 | 0 | 3000 | 0 | High Voltage Breaker, Inc. | HVB-550-400000-0, sn550A2009-205 | 0 | Bushing has flange bolted to CB body. | Units anchored with about a foot of weld (only one side could be seen in picture) to a cast in place embedment. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 81200 | No | 0 | 0 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 4 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Structure/WT | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1992-01-02 | 0 | 0 | 0
SS#26 | Undamaged | 3 | Coupling Voltage Trans. CVT | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | These were adjacent to dead-tank CB. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1992-01-02 | 0 | 0 | 0
SS#26 | Damaged | 6 | Coupling Voltage Trans. CVT | CC5 | 0 | 0 | 0 | 0 | Structure/WT | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on lattice structure with WT. Two may not have had WTs. Units after they were repaired or replaced: 5 GE with 3 porcelain segments and 1 (WE?) with 4 porcelain segments. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 2 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522A | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Units had flexible connects to CB. Units held with friction clips. Support structure very flexible. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 3 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622A & B | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Units had rigid connects to CB. Units held with friction clips. Support structure very flexible. | Porcelain failed near top. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 7 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Units had flexible connects to CB. Units held with friction clips. Support structure very flexible. | Ceramic failed near top in most cases. In one case it failed about middle. One unit toppled from pad. Some failures may be due to secondary damage when CB failed. Bus connections to CB on several units fail at CB side, presumably after porcelain fai | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 108 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | damage unkown | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-20 | 0 | 0 | 0
SS#26 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Just the post insulator on the contact side failed. It was connected to the bus that fell. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | unit adjacent to the dead tank CB had the blade misaligned. It is not know if it was functional. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 2 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 775 | 500 | 0 | 0 | 0 | Southern States | 0 | 0 | 0 | 0 | The insulator on the contact side had bolts fail at base of post. Inadequate thread penetration. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 5 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | One or both of the post insulators on the hinge side failed and the post insulator in the contact side also failed. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 7 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | One or both of the post insulators on the hinge side failed and the post insulator in the contact side did not fail. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 8 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | One or both of the post insulators on the hinge side failed and the post insulator in the contact side did not fail. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 112 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 17 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 1 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus supported. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 102 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 1 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus supported. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 12 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus supported, bus sectioning switch. | It appears these DS were pulled apart by the out of phase dynamic response of adjacent bus sections | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 121 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 1 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus supported , bus sectioning switch. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus supported. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 119 | 1991-11-26 | 0 | 0 | 0
SS#26 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus supported. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 120 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 114 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Supported on its own structure. | Not sure if any of these were damaged. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 150 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 4 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on radiator of 500/230 kV TR, Bank 9. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 4 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on 230/115 kV Bank 8. It is mounted on radiator. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 101 | 1991-11-26 | 0 | 0 | 0
SS#26 | Undamaged | 4 | Lightning Arrester LA | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lattice-type post support. Adjacent to 500/230 kV TR, Bank 9. | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 100 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 1 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 1C | 230 | 115 | 0 | 0 | General Electric | 0 | 1989 | 0 | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-17 | 0 | 0 | 0
SS#26 | Undamaged | 8 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 1, 2, 3 | 230 | 115 | 0 | 0 | General Electric | 0 | 1950 | 0 | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-17 | 0 | 0 | 0
SS#26 | Undamaged | 2 | Transformer TR | TR1 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 8 | 230 | 115 | 0 | 0 | McGraw Edison | OA, FOA, FOA, sn C04169-5-2 | 1972 | 11270 g of oil with wt of 84500, rad stick out 66", have large rad supports and relatively small rad. There is tertiary 13200 winding. Each TR has 5 bushings. Tertiary bus looks very flexible and there is little slack to bushings and LA. Note TR for | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts. | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 285000 | No | 0 | 293 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 1 | Transformer TR | TR1 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 115 | 0 | 0 | McGraw Edison | OA, FOA, FOA, sn C04169-5-2 | 1972 | 11270 g of oil with wt of 84500, rad stick out 66", have large rad supports and relatively small rad. There is tertiary 13200 winding. Each TR has 5 bushings. Tertiary bus looks very flexible and there is little slack to bushings and LA. Note TR for | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts. | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 285000 | No | 0 | 293 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 4 | Transformer TR | TR3 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 9 | 500 | 230 | 0 | 0 | McGraw Edison | Spec. 13135-A, sn C05322--5-1 (single phase) | 1978 | Rad. are are mounted on 3 sides, each with large box beam perp. to TR body with 4 rad. cores on each side of beam. Over all rad. is 68" out and 138" along TR. Lower rad support is large box beam that has no diagonal bracing but there are horizontal supp | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts. | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 489300 | No | 0 | 0 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 1 | Transformer TR | TR4 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 12 | 0 | 0 | Westinghouse | FO, FA, three phase | 0 | 8020 g . TR is tall with small foot print. (about 13' x 13'). While rad are not very heavy, upper penetration supports total weight. | anchored by welding to embedment but angles are bolted to TR with what looks like small bolts. | original pictures indicate that one had small oil leak at rad. | No impact on service. They may have been repaired by tightening bolts. | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 431100 | No | 0 | 0 | 1991-12-19 | 0 | 0 | 0
SS#26 | Undamaged | 4 | Transformer TR | TR1 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 13.8 | 0 | 0 | McGraw Edison | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-20 | 0 | 0 | 0
SS#26 | Undamaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator Mount | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Each WT is about 2' in diameter and 2' long. | Mounted on structure with CVT | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1992-01-02 | 0 | 0 | 0
SS#26 | Undamaged | 3 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator Mount | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Each WT is about 2' in diameter and 3' long. | Mounted on structure with CVT | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 306 | 1992-01-02 | 0 | 0 | 0
SS#26 | Damaged | 2 | Wave Trap WT | WT2 | 0 | 0 | 0 | H. Post-Insulator Mount | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Each WT is about 3' in diameter and 5' long. Insulators are tapered. | Mounted on lattice structure with CVT | porcelain supports failed | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-20 | 0 | 0 | 0
SS#26 | Undamaged | 4 | Wave Trap WT | WT2 | 0 | 0 | 0 | H. Post-Insulator Mount | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Each WT is about 3' in diameter and 5' long. Insulators are tapered. | Mounted on lattice structure with CVT | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-28 | 0 | 0 | 0
SS#26 | Damaged | 1 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | bus on site was 4 1/2 and 8 dia. al. pipe. West bus. Each bus has 6 insulator supports, each with 6 tapered sections. | 0 | All post insulators supporting B phase bus failed, dropping the bus. Connector between top of post insulator and bus may have been weak spot. Some units failed at connection and some had porcelain failure. This was bus B phase on west side of site. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 1200 | 0 | 1991-12-28 | 0 | 0 | 0
SS#26 | Damaged | 1 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | East 3 phases of bus is 8". After earthquake there are 15 supports with 6 tapered elements, 7 with 2 elements, and 2 with 3 elements. | 0 | One insulator supporting one bus C on east side of site failed, the bus dropped but did not fall or malfunction. | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 1200 | 118 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 2 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 1200 | 0 | 0 | 0 | 0 | West bus, A and C phase did not fail. Bus 8" diameter pipe, with 6 insulators per bus, each with 6 tapered sections. | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-12-28 | 0 | 0 | 0
SS#26 | Undamaged | 2 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 1200 | 0 | 0 | 0 | 0 | East 3 phases of bus is 8". After earthquake there are 15 supports with 6 tapered elements, 7 with 2 elements, and 2 with 3 elements. 8 insulators per bus. | 0 | 0 | 0 | (UBC S2) >2000 ft alluvium with some <20 ft soft clay layers overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 106 | 1991-12-28 | 0 | 0 | 0
SS#28 | Undamaged | 12 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200, 230, 270, 680, | 230 | 0 | 0 | 0 | General Electric | oil | 0 | 0 | 0 | 0 | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#28 | Undamaged | 9 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610, 850, 860 | 230 | 0 | 0 | 0 | Westinghouse | oil | 0 | 0 | 0 | 0 | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#28 | Undamaged | 21 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240, 660, 800, 810, 820, 870, 880 | 230 | 0 | 0 | 0 | Allis Chalmers | oil | 0 | 0 | 0 | 0 | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#28 | Damaged | 2 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB 4 or 6 | 0 | 0 | 0 | Support column gasket leaks. | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#28 | Undamaged | 7 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB 4 or 6 | 0 | 0 | 0 | 0 | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#28 | Undamaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 9 | 230 | 115 | 0 | 0 | General Electric | 0 | 1986 | 0 | 0 | 0 | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-17 | 0 | 0 | 0
SS#28 | Undamaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 11 | 230 | 115 | 0 | 0 | Westinghouse | 0 | 1965 | 0 | 0 | 0 | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-17 | 0 | 0 | 0
SS#28 | Undamaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 7 | 230 | 115 | 0 | 0 | Westinghouse | 0 | 1974 | 0 | 0 | 0 | 0 | (UBC S3) >500 ft alluvium/estuarine with some >20 ft bay mud layers overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | No | 0 | 0 | 1998-07-17 | 0 | 0 | 0
SS#39 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | Air supply looked good. Lowest porcelain on CT support column failed. | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 2 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 6 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7, ATB-242-43000-7 | 0 | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | This equipment was only viewed after it was in bone yard, so specific equipment could not be associated with specific dispatch positions, and parts could not always be associated with a single phase. It is assumed that at least one support column usuall | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 24 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212, 222, 252, 262, 342, 372, 712, 722 | 230 | 0 | 0 | 0 | Westinghouse | Oil | 0 | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | This equipment was only viewed after it was in bone yard, so specific equipment could not be associated with specific dispatch positions, and parts could not always be associated with a single phase. It is assumed that at least one support column usuall | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 3 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB 4 230-15000-4 | 0 | 0 | 0 | Do not have any details on damage of these units. | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 2 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | mounted on lattice structure that supported WT and CVT. | CVT porcelain column broke at base of column. | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 1 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | may be more than one | Mounted on lattice structure with WT. There was at least one other. | how many were undamaged, and what was installation. | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | The insulators were cap&pin type (Victor) | These units were supported high on the bus support structure, they were probably CB disconnect switches. They were mounted with the porcelain in the horizontal position. | There were two failures of post insulators. | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 5 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | There were one to three type of failures. In one, a weld that connects the base of the plate that is bolted to the bottom flange of the post insulator failed so that no torque could be applied to the column to change the position of the switch. There w | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | How many undamaged switches were there and how were they mounted? | 0 | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | The insulators were cap&pin type. | These units were supported high on the bus support structure, they were probably CB disconnect switches. They were mounted with the porcelain in the horizontal position. | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 4 | Lightning Arrester LA | LA1 | 0 | 0 | TR Body Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on body of 230/115 kV McGraw Edison TR Bank 7 | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | TR Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mounted on General Electric TR Banks 5 & 6. It is not clear how they are mounted - body or boom. | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 3 | Transformer TR | TR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | Seven TRs mounted on large elevated pads. Three mounted with bolts that were grouted in along sides of pad through large angle came lose. This was an old installation. The grout had the consistency of very weak plaster of Paris. | 0 | The was no impact of operations. | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 4 | Transformer TR | TR1 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 7 | 230 | 115 | 0 | 0 | McGraw Edison | 0 | 0 | photo page 3-74 of EPRI NP-7500-SL | 0 | Replace seals at upper connection to stop leaking. Not sure how many leaks. I think there were 4 TRs. On return visit I thought that deformation of lower support was recorded but I could not find it in my slides. | Excavate to remove soil that had absorbed spilled oil. | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 6 | Transformer TR | TR1 | 0 | Med Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 5 & 6 | 230 | 115 | 0 | 0 | General Electric | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 2 | Miscellaneous | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Section of rigid bus that passes over bus support structure and forms connection between flexible bus and CB had its end casting fail. | 0 | 0 | The fallen bus fell on flexible bus of three phases. | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 2 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Hook connection between strain bus and bus support structure became unhooked and dropped bus. | 0 | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 2 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Transfer bus. | 0 | Post insulators supporting a section of transfer bus failed, allowing the bus to fall in one case or drop in another | The fallen bus fell on flexible bus of three phases. | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Undamaged | 0 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Transfer Bus | 0 | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 1 | Miscellaneous | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Section of rigid bus that that connects to flexible bus to by-pass CB on top of support structure had its end casting fail, allowing rigid bus to swing and come in contact with bus support structure. | 0 | 0 | The fallen bus fell on flexible bus of three phases. | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#39 | Damaged | 1 | Synchronous Condensor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Synchronous Condenser. When I visited the site, it looked like one of the units was being worked on. There was a portable nitrogen supply connected to the units. There may have been a gas leak. | 0 | 0 | 0 | (UBC S2) <20 ft bay mud overlying >200 ft alluvium/estuarine overlying metavolcanic rock, (NEHRP E - soft clay Vs<=180 m/s) | 0 | No | 0 | 82 | 1991-11-26 | 0 | 0 | 0
SS#20 | Damaged | 1 | Circuit Switcher CS | CS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 115 | 0 | 0 | 0 | S & C | 0 | 0 | Circuit switcher 115 kV | 0 | Blew up. | CB 112 relayed on fault pressure. There was not test made. Bank was inspected, looked OK and CB closed @ 1410. At 1425 117 blew up and CB 112 isolated station. Cleared 117 and picked up one bank. | 0 | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB15A | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832 | 500 | 0 | 4000 | 0 | Allis Chalmers | ABM SN 11714 | 1965 | 0 | 0 | Aluminum casting that supports the interrupter head failed. | Out of service for 4 days - no effect on service. | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Undamaged | 2 | Circuit Breaker CB | CB15A | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832 | 500 | 0 | 4000 | 0 | Allis Chalmers | ABM SN 11714 | 1965 | seismic specification was 0.2g static horizontal. | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Undamaged | 6 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272, 282 | 230 | 0 | 0 | 0 | Westinghouse | 2300SF1500 | 1967 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#21 | Undamaged | 3 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 230 | 0 | 0 | 0 | Pen | Oil, RHE90 | 1966 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications, original specifications was .2g horizontal - static | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | Interrupter head support column adjacent to CT failed - lowest ceramic member cracked. 4 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 2 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Undamaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | Cracked interrupter head support column adjacent to CT. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Undamaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 18 | 1991-11-26 | 0 | 0 | 0
SS#21 | Undamaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 19 | 1991-11-26 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN Z 62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 1 damaged guy. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 6 hrs to repair guy at a convenient time. | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 3 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 2 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Damaged | 1 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is more rigid than x2x units. Both welded and friction clip anchorage. Installed in 1968. | 1 damaged guy - next to CT. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Undamaged | 8 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842, 942 | 500 | 0 | 3000 | 0 | Westinghouse | SF6 500SF35000, SN 3-62Y5007 | 1965 | No Seismic modifications | Rigid connection between CB and CT, CT support is more rigid than x2x units. Both welded and friction clip anchorage. Installed in 1968. | It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#21 | Undamaged | 6 | Circuit Breaker CB | CB15 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 732, 932 | 500 | 0 | 0 | 0 | General Eelctric | ATB 500380001K | 1968 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-07-20 | 0 | 0 | 0
SS#21 | Undamaged | 18 | Circuit Breaker CB | CB74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212, 222, 232, 242, 252, 262 | 230 | 0 | 0 | 0 | 0 | Unknown | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#21 | Undamaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 3 A, B, C | 230 | 70 | 0 | 0 | 0 | single phase | 1967 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#21 | Undamaged | 3 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 1 A, B, C | 500 | 230 | 0 | 0 | 0 | single phase | 1967 | 0 | 0 | 0 | 0 | (UBC S1) < 200 ft alluvium overlying metavolcanic rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#24 | Undamaged | 15 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF6 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 137 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 12 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382, 262, 232, 252 | 230 | 0 | 0 | 0 | 0 | Oil | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#24 | Damaged | 1 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812B | 500 | 0 | 3000 | 0 | Westinghouse | SF6, 500SF35000,SN 3-62405041 Seis reinforced 1973 | 1966 | Seismically strengthened 1973 by replacing wood tendons with fiberglass. Originally were 0.2g static horizontal. Note that SCE seismic units also have dampers. | Anchor bolts securing friction clips on 6 legs stretched or pulled out slightly. Adjacent current transformers had tit-tat-toe chair support that was flexible and there were signs of distress in cracked paint but no permanent deformations. Rigid connec | Interrupter head near CT failed explosively and with internal part of interrupter severely burned. There was not significant shifting of CB on its pad. There may have been vertical impact due to stretch or pullout of anchor bolts. Motion of CT may hav | 9 days to restore, did not cause disruption. | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 130000 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 11 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722, 822, 922, 812 A&C | 500 | 0 | 3000 | 0 | Westinghouse | SF6, 500SF35000,SN3-624-5041 Seis | 1966 | Seismically strengthened 1973 by replacing wood tendons with fiberglass. Originally were 0.2g static horizontal. Note that SCE seismic units also have dampers. | Anchor bolts securing friction clips on 6 legs stretched or pulled out slightly. Adjacent current transformers had tit-tat-toe chair support that was flexible and there were signs of distress in cracked paint but no permanent deformations. Rigid connec | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 130000 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 15 | Circuit Breaker CB | CB74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222, 242, 212, 312,292 | 230 | 0 | 0 | 0 | 0 | Unknown | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-06-12 | 0 | 0 | 0
SS#24 | Undamaged | 6 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB6 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | CB Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 143 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 0 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 0 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Structure/WT | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 5 | Coupling Voltage Trans. CVT | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 12 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 24 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 127 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 6 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Don't know how many but there are at least 6 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Damaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric 192 | 9L11AW736 Alugard | 1964 | Pictures indicate that there was a short porcelain section at base with a coupling to a long upper section. | Mounted on boom on 230/115 Pennsylvania TR | The short lower porcelain member of LA that failed. | 6 hours to repair, no effect on operation at site | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Pictures indicate that there was a short porcelain section at base with a coupling to a long upper section. | Mounted on boom on 230/115 Pennsylvania TR | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 7 | Lightning Arrester LA | LA1 | 0 | 0 | TR Body Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | mounted on body of 500/230 kV TR | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 7 | Lightning Arrester LA | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Associated with 500/230 kV TR | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 134 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 8 | Transformer TR | TR1 | 0 | Med Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 115 | 0 | 0 | Pennsylvania | Spec. 10035, sn 0-02265-5-3 | 1950 | Rad. elements supported from tank. C&C 94700, T&F 64400, 6970 g - 54300. | 230 LA on boom, 115 LA on rad. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 211400 | 0 | 0 | 0 | 1998-07-08 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank 1, 2, 2 | 230 | 115 | 0 | 0 | Westinghouse | single phase | 1968 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1998-07-08 | 0 | 0 | 0
SS#24 | Undamaged | 1 | Transformer TR | TR3 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | McGraw Edison | Spec. 13330, sn C06503-5-7 | 1968 | Large radiators with each element supported from maniford perp. to TR tank. 70" X 127" along TR. They are supported on non-penatrating pipe at bottom and penetrating pipe at top. There are horizontal braces at bottom but not consistant (one brace was | 230 LA on rad. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 490300 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 3 | Transformer TR | TR3 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | General Electric | OA, FA, FO, sn D577035, -6, 7 | 1968 | 2 large radiators per side with each element supported from heavy box beam perp. to TR body and with non-penatrating connection with gusset plates for vert. load. Top connection is penertatng pipe. Each 142" long. There are diagonal braces at bottom, | West end of TR row. 230 kV LA installed on rad. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 600000 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 3 | Transformer TR | TR3 | 0 | Large Rad/O Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | Westinghouse | OA, FA, FO, Core Type | 1968 | Large radiators with each element supported from a TR tank. Rad. on sies and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 230 LA on boom. 500 LA on independent lattice structure. Units 1, 2 and 4 from east end of site. | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 606000 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#24 | Undamaged | 4 | Wave Trap WT | WT2 | 0 | 0 | 0 | H. Post-Insulator Mount | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | (UBC S1) < 30 ft alluvium overlying sedimentary rock, (NEHRP D - stiff soil 180m/s<Vs<=360 m/s) | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#7 | Undamaged | 9 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | ITE "watch bob" gas type | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 24 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | vertical tank type oil circuit breakers | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Circuit Breaker CB | CB5 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB 912 - Palo Verde Line | 500 | 0 | 0 | 0 | Cogenel | air blast | 0 | flexible conductors, dynamic analysis 0.5 g PGA design specification | mounted on steel A-frame w/ horizontal pressure vessel, breaker head mounted on 30 ft high columns (diagonally braced) consisted of 3 large spherical mufflers, 4 tripping resistors, 2 capacitors, 2 extinguishing chambers | completely destroyed, diagonal and vertical insulators failed, breaker heads fell | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Circuit Breaker CB | CB5 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB 712 - Palo Verde Line | 500 | 0 | 0 | 0 | Cogenel | air blast | 0 | flexible conductors, dynamic analysis 0.5 g PGA design specification | mounted on steel A-frame w/ horizontal pressure vessel, breaker head mounted on 30 ft high columns (diagonally braced) consisted of 3 large spherical mufflers, 4 tripping resistors, 2 capacitors, 2 extinguishing chambers | completely destroyed, diagonal and vertical insulators failed, breaker heads fell | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 3 | Circuit Breaker CB | CB73 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB 922 | 500 | 0 | 0 | 0 | Westinghouse | puffer | 0 | flexible conductors, dynamic analysis 0.5 g PGA design specification | no horizontal pressure vessel, no mufflers in breaker head | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Circuit Breaker CB | CB9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB4032 | 220 | 0 | 0 | 0 | GE | ATB4-6 SF6 | 0 | 0 | supported on steel frame | 2 column insulators broken , tank damage and corona ring broken | replaced | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Circuit Breaker CB | CB9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB4102 | 220 | 0 | 0 | 0 | GE | ATB4-6 SF6 | 0 | 0 | supported on steel frame | 2 column insulators shattered | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 2 | Coupling Voltage Trans. CVT | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Trench Electric & GE | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1998-10-08 | 0 | 0 | 0
SS#7 | Damaged | 4 | Coupling Voltage Trans. CVT | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Trench Electric & GE | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 1 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB 922 | 500 | 0 | 0 | 0 | Alsthom | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#7 | Damaged | 2 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB 922 | 500 | 0 | 0 | 0 | Alsthom | 0 | 0 | 0 | 0 | B & C broken , failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB 912 | 500 | 0 | 0 | 0 | Alsthom | 0 | 0 | 0 | 0 | A in half, B&C broken at flange, failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Current Trans. CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CB 712 | 500 | 0 | 0 | 0 | Alsthom | 0 | 0 | 0 | 0 | failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 9 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | Porter & Brown Boveri | 0 | 0 | 0 | 0 | Brown Boveri failed on jaw side at base of insulators, Porter failed on hinge side in the porcelain | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 3? | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | Siemens-Allis | AVB4 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 2500 lb on hinge support, 3500 lb on jaw support | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 15 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 500 | 0 | 0 | 0 | Porter & Brown Boveri | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bank | 0 | CB 5032 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Supported on steel frame | destroyed, A phase broke at mounting flange for insulators | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | line | 0 | CB 5032 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Supported on steel frame | damaged, C phase out of adjustment would not open | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bus | 0 | Hinds-CB 6022 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Supported on steel frame | A phase damaged, conductors from bus disconnects to bus stiffening insulators broke at base | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | position no. 3, Vista #1 T/L CB 6032 | 220 | 0 | 0 | 0 | Brown Boveri | line side of CB 6032, single blade | 0 | 0 | Supported on steel frame | destroyed, broke at disconect flange all three phases | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 84 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Supported on steel frame | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Lightning Arrester LA | LA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1A Bank | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | destroyed, all three phases broke at base | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 2 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#7 | Damaged | 2 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4A Bank | 220 | 0 | 0 | 0 | GE | ALUGARD 9L11LBA1B | 0 | 0 | 0 | destroyed, A & B phase broke at base | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 2 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3A Bank | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | destroyed, A & B phase broke at base | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2A Bank | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | destroyed, all three phases broke at base | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 1 | Lightning Arrester LA | LA5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Ohio Brass | MPR Series F | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#7 | Damaged | 9 | Lightning Arrester LA | LA5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Ohio Brass | MPR Series F | 0 | 0 | 0 | destroyed, all broken at base of porcelain, may have been caused by swinging of wave traps which they were attached to by conductors | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Position no. 10, so. 220 kV Bus | 220 | 0 | 0 | 0 | GE | CD31023 SINGC | 0 | 0 | 0 | destroyed, broke at base of bushing | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Position no. 10, no. 220 kV Bus | 220 | 0 | 0 | 0 | GE | CD3123 SINGC | 0 | 0 | 0 | destroyed, broke at base of bushing | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 4 | Potential Trans. PT | PT5 | 0 | 0 | 0 | 0 | 0 | Line | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | GE Pot Dev CC | 4CD52A505C6C | 0 | 0 | 0 | destroyed | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 6 | Potential Trans. PT | PT5 | 0 | 0 | 0 | 0 | 0 | Bus | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | W. Pot. Dev Type FCA | 0 | destroyed | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 4 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1A, 2A, 3A, 4A | 200 | 115 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | leaking oil around seals on bushings at the top of transformers, L-shaped connectors stressed beyond elestic limit at base causing transformers to walk and rock | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 1 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1AA bank | 500 | 220 | 0 | 0 | Allis-Chalmers | single phase | 0 | 0 | 500 kv bushing W Type O EBM 1675, concrete pad, anchored by steel gusset plates connected to concrete by 1" bolts and hooked over base flange | leaking oil around seals on bushings at the top of transformers, 1" bolts sheared at base causing transformers to walk (8" to 10") and rock | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1AA bank | 500 | 220 | 0 | 0 | Westinghouse | single phase | 0 | 0 | 500 kv bushing W Type O EBM 1675, concrete pad, anchored by embeded steel gusset plates hooked over base flange | leaking oil around seals on bushings at the top of transformers, L-shaped connectors stressed beyond elastic limit at base causing transformers to walk and rock | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 2 | Wave Trap WT | WT2 | 0 | 0 | 0 | Hanging | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | GE | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 2 | Wave Trap WT | WT2 | 0 | 0 | 0 | Hanging | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | GE | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 3 | Motor Operated Disconnect Switch MODS | MODS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | Siemens-Allis | single blade | 0 | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#7 | Damaged | 1 | Motor Operated Disconnect Switch MODS | MODS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOD 4041, 2A Bank | 220 | 0 | 0 | 0 | Siemens-Allis | single blade | 0 | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assembly broke off at base on A phase | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 3 | Motor Operated Disconnect Switch MODS | MODS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOD 6063 3A Bank | 220 | 0 | 0 | 0 | Siemens-Allis | single blade | 0 | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assemblies fell to ground on all three phases | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 2 | Motor Operated Disconnect Switch MODS | MODS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOD 6073 4A Bank | 220 | 0 | 0 | 0 | Siemens-Allis | single blade | 0 | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assembly broke off at base on A phase | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 2 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | on top of A-frame racks supporting rigid jumper bus tie | 2 insulators failed at base dropping rigid bus and twisting flexible conductors. | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Damaged | 64 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | bus suspension insulators | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 8 | Post Insulator PI | PI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#7 | Damaged | 70 | Post Insulator PI | PI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | supported bus conductors | 0 | may have been caused by slack bus conductor strung from post to post | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#7 | Undamaged | 2 | Shunt Reactor | SR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | GE | OA-MS | 0 | 0 | concrete pad, anchored by embeded steel gusset plates hooked over base flange | 0 | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#7 | Damaged | 4 | Shunt Reactor | SR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | GE | OA-MS | 0 | 0 | concrete pad, anchored by embeded steel gusset plates hooked over base flange | three types of failure, 1) rocking, 2) excessive movements of reactor bushings causing oil leaks, 3) terminal connector at top of bushing pulled off | 0 | Quaternary formation - alluvial fan deposits | 0 | Yes | 0 | 0 | 1986-07-08 | 0 | 0 | 0
SS#40 | Undamaged | 54 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5012, 5022, 5042, 5072, 5082, 5092, 5102, 5112, 4082, 4092, 6012, 6022, 6042, 6072, 6082, 6092, 6102, 6112 | 230 | 0 | 0 | 0 | 0 | Oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#40 | Undamaged | 108 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#40 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#40 | Undamaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2A, 4A | 230 | 66 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 63 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 12 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 150 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 24 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 7 | Transformer TR | TR1 | 0 | Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 14 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 6 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1A, 2A | 220 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 6 | Transformer TR | TR2 | 0 | Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1, 2, 3, 4, 5, 6 | 220 | 14 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 6 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 12 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | Oil | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 42 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 401, 603 and either side of 432, 422, 412, 632, 622, 612 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Damaged | 1 | Lightning Arrester LA | LA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How is it installed | porcelain failed. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#8 | Undamaged | unk | Lightning Arrester LA | LA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How is it installed | porcelain failed. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#8 | Undamaged | 7 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 7 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4A, 3A | 220 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#18 | Undamaged | 54 | Circuit Breakers CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4142, 4122, 4112, 4102, 4097, 4062, 1052, 4042, 4032, 6142, 6122, 6112, 6102, 6097, 6062, 6052, 6042, 6032 | 220 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#18 | Undamaged | 108 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | either side of 4142, 4122, 4112, 4102, 4097, 4062, 1052, 4042, 4032, 6142, 6122, 6112, 6102, 6097, 6062, 6052, 6042, 6032 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#18 | Undamaged | 15 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#18 | Undamaged | 5 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1A, 2A, 3A, 4A | 220 | 66 | 0 | 0 | 0 | 3 phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#18 | Undamaged | 1 | Synchronous Condensor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Synchronous Condenser | 0 | misalignment causing loss of bearing pressure | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#18 | Damaged | 3 | Synchronous Condensor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Synchronous Condenser | 0 | misalignment causing loss of bearing pressure. Some could continue to run. | one replace bearing and others realign. | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#19 | Undamaged | 39 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#19 | Undamaged | 3 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | Oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#19 | Undamaged | 5 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB | 0 | Model not shown in data. | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#19 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB | 0 | Model not shown in data. | 0 | leaking support column gaskets | N restored Feb 13, S restored Feb 26 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#19 | Undamaged | 102 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#19 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#19 | Undamaged | 6 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#19 | Damaged | 2 | Synchronous Condensor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Synchronous Condensers | 0 | loss of pressure, misaligned and bearing damage | realign bearings | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#19 | Undamaged | unk | Synchronous Condensor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Synchronous Condensers | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 280 | 1991-12-10 | 0 | 0 | 0
SS#23 | Damaged | 1 | Synchronous Condensor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | synchronous condenser | 0 | loss of oil pressure | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#23 | Undamaged | 0 | Synchronous Condensor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | synchronous condenser | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
Misc | Damaged | 9 | Circuit Breaker CB | CB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 damaged bushings at Solemint and 3 flash overs at Saugus | 0 | 0 | 0 | 0 | 0 | 0 | 1991-12-10 | 0 | 0 | 0
Misc | Damaged | 4 | Disconnect Switch DS | DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Disconnect switches missaligned at Citrus SS and porcelain damage at Newhall | 0 | 0 | 0 | 0 | 0 | 0 | 1991-12-10 | 0 | 0 | 0
Misc | Damaged | 0 | Miscellaneous | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Several transmission towers on several lines had to have footings or foundations compacted. While some were under construction, most were existing in-service towers. There was no disruption from these failures. | 0 | 0 | 0 | 0 | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#41 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H. Swing-Tripod | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | use of tripod support | post insulator failed at base. In falling it pulled the bayonet and corona ring wich burned the operating rod. This is refered to as secondary damage. | Control rod and 3 post insulators were replaced. | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H. Swing-Tripod | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | 0 | 0 | Broken post insulator on line side. Unit opened and reclosed with bayonet on top of the bell on the female half of disconnect. | Replace insulator. | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Broken post insulator on line side. Reported as secondary damage. Need to review station for assessment. | Replace insulator. | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Undamaged | unk | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Undamaged | unk | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | H. Swing-Tripod | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Damaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From picture, the LA appears to be on line between OCB and DS, an unusal situation. | porcelain failed at base | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-10-29 | 0 | 0 | 0
SS#41 | Undamaged | 1 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shifted on transfer car and slipped its rail chocks about 6 inches | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Damaged | 1 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 kV bushing cracked, fell over and cracked bowl on its top. | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Undamaged | 5 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Four units sheared anchor bolts on one side and shifted 1 to 2 inches | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Damaged | 1 | Capacitor Racks CR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | support insulator broke. Rack pulled towards bus about 4" and three bus side bushings on 16 kV capacitor PCB flashed over and were replaced. | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#41 | Damaged | 1 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | Transfer bus on 2A Bank | 0 | Fitting on transfer bus support failed allowing one end of bus to fall. Porcelain did not fail. | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-06 | 0 | 0 | 0
SS#44 | Undamaged | 0 | Circuit Breaker CB | CB9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | GE | ATB | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1999-03-25 | 0 | 0 | 0
SS#44 | Damaged | 33 | Circuit Breaker CB | CB9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | GE | ATB | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1999-03-25 | 0 | 0 | 0
SS#44 | Undamaged | 2 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1999-03-25 | 0 | 0 | 0
SS#44 | Damaged | 3 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | remained on supports with damage to oil seals, terminal taps and base connections | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1999-03-25 | 0 | 0 | 0
SS#44 | Damaged | 7 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | broke from steel post support pedestal and fell to ground | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1999-03-25 | 0 | 0 | 0
SS#45 | Undamaged | 12 | Circuit Breaker CB | CB15 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | GE | ATB | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#45 | Undamaged | 48 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF6 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#45 | Undamaged | 9 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Westinghouse | SF6 non-seismic | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#45 | Damaged | 3 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Westinghouse | SF6 non-seismic | 0 | Vincent is not on data sheets | 0 | Individual data is not vailable. 3 porcelain columns failed, 2 columns cracked of the 9 columns, 10 of 18 porcelain guys failed. 5 of 9 twisted clockwise as view from above. | 41 days before spares could be obtained. | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#45 | Damaged | 6 | Circuit Breaker CB | CB72 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Westinghouse | SF6 non-seismic | 0 | Vincent is not on data sheets | 0 | 4 porcelain guys on N and 7 guys on S failed. | Guy damage would not effect operation. Units were repaired and put back into service within 48 hrs. | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#45 | Undamaged | 96 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-10-08 | 0 | 0 | 0
SS#45 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Vincent is not on data sheets. What is type? | How is it installed? | Post insulator failed. Unit out of alignment. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#45 | Undamaged | 17 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Probably don't have all DS1 | How is it installed? | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#45 | Damaged | 1 | Lightning Arrester LA | LA5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Vincent is not on data sheets | How is it installed? | porcelain failed. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#45 | Undamaged | 10 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#45 | Undamaged | 24 | Lightning Arrester LA | LA5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Vincent is not on data sheets | How is it installed? | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#45 | Undamaged | 8 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-10-28 | 0 | 0 | 0
SS#45 | Damaged | 1 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | 0 | 0 | Vincent is not on data sheets | 0 | Radiator leak. | restoration? | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#45 | Damage | 1 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | 0 | 0 | Vincent is not on data sheets | 0 | LA damaged radiator fan. | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 261 | 1991-12-10 | 0 | 0 | 0
SS#45 | Damaged | 2 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Bus support | How is it installed? | 2 post insulators failed. How many did not fail? | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 266 | 1991-12-10 | 0 | 0 | 0
SS#45 | Undamaged | 106 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Bus support | How is it installed? | 2 post insulators failed. How many did not fail? | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1991-12-10 | 0 | 0 | 0
SS#13 | Undamaged | 12 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | Oil | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#13 | Undamaged | 36 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#13 | Undamaged | 12 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#13 | Undamaged | 6 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | Low Seismic | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#13 | Damaged | 1 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | General Electric | 8275998 | 0 | Single phase 220/66 kV TR. | 0 | 220 bushing gasket leaks. Anchorage was distressed. | Replace 220 kV bushing on 220/66 kV B phase TR. | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1991-12-07 | 0 | 0 | 0
SS#13 | Undamaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | General Electric | 8276000, -1, -2 | 0 | Single phase 220/66 kV TRs. | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1991-12-07 | 0 | 0 | 0
SS#13 | Undamaged | 2 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | General Electric | 8275997, -9 | 0 | Single phase 220/66 kV TRs. | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1991-12-07 | 0 | 0 | 0
SS#13 | Damaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | Westinghouse | 3418517, -8, -9 | 0 | Single phase 220/66 kV TRs. | 0 | 220 bushing gasket leaks. Anchorage was distressed. | Replace each 220 kV bushing on each single phase 220/66 kV TR. | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1991-12-07 | 0 | 0 | 0
SS#13 | Damaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | Westinghouse | 3772575, 4088092,-3 | 0 | Single phase 220/66 kV TRs. | 0 | 220 bushing gasket leaks. Anchorage was distressed. | Replace each 220 kV bushing on each single phase 220/66 kV TR. | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 1991-12-07 | 0 | 0 | 0
SS#14 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | One of the outside interrupter head bushing blew. From slack that was available it appears that head moved about 12". | 0 | Quaternary formation - soil | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#14 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | Crack at sandring allowed SF6 to leak out. | Lower porcelain member had to be replaced. | Quaternary formation - soil | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#14 | Damaged | 3 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | Porcelain interrupter head support columns failed. | Dead tank replacement unit used. | Quaternary formation - soil | 0 | 0 | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#14 | Undamaged | 7 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | 0 | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#14 | Undamaged | 2 | Transformer TR | TR2 | 0 | 3 phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | 0 | 0 | 0 | 1998-10-09 | 0 | 0 | 0
SS#14 | Undamaged | 30 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | 0 | 0 | 0 | 1998-04-02 | 0 | 0 | 0
SS#9 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 1600 | 0 | General Electric | ATB7 | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 1600 | 0 | General Electric | ATB7 | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | Only one of the gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 3000 | 0 | General Electric | ATB7 | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Interrupter head support column failed (column w/o CT) | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 3000 | 0 | General Electric | ATB7 | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 3000 | 0 | General Electric | ATB7 (isolated) | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. Unit mounted on 3/4" elastomer pad | Only one gaskets on the 2 interrupter head bushings that were connected to each other blew. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Undamaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 3000 | 0 | General Electric | ATB7 (isolated) | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. Unit mounted on sock isolators of | 0 | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Damaged | 2 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 3000 | 0 | General Electric | ATB7 | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Damaged | 3 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 1600 | 0 | General Electric | ATB7 | 1971 | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts. | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Undamaged | 7 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 1600 | 0 | General Electric | ATB7 | 1971 | Same as for damaged units | Same as for damaged units | 0 | 0 | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Damage | 1 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | low design | 0 | 0 | 0 | 0 | 0 | Firm | 0 | Yes | 0 | 0 | 1991-11-26 | 0 | 0 | 0
SS#9 | Undamaged | 77 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | low design | 0 | 0 | 0 | 0 | 0 | Firm | 0 | Yes | 0 | 0 | 1998-04-09 | 0 | 0 | 0
SS#9 | Undamaged | 24 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Firm | 0 | Yes | 0 | 0 | 1998-04-09 | 0 | 0 | 0
SS#9 | Damaged | 1 | Transformer TR | TR2 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | three phase | 0 | 0 | Well anchored | Minor oil leak at top connection of radiator to tank. | 0 | Firm | 0 | Yes | 0 | 124 | 1991-11-26 | 0 | 0 | 0
SS#9 | Undamaged | 7 | Transformer TR | TR2 | 0 | Large Rad/Manif | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | three phase | 0 | 0 | Well anchored | 0 | 0 | Firm | 0 | Yes | 0 | 125 | 1991-11-26 | 0 | 0 | 0
SS#1 | Undamaged | 63 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB4 | 0 | 0 | 0 | CT leak on C phase | Completed 10/2.87 @ 0339 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#1 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric? | ATB4? | 0 | 0 | middle phase | Leaking nin-CT column | Completed 10/5/87 @ 1200. Note that it was after aftershock. | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#1 | Undamaged | 10 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB 4-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#1 | Undamaged | 150 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-23 | 0 | 0 | 0
SS#1 | Undamaged | 24 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-23 | 0 | 0 | 0
SS#1 | Undamaged | 7 | Transformer TR | TR1 | 0 | Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 14 | 0 | 0 | 0 | single phase, unit | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-24 | 0 | 0 | 0
SS#1 | Undamaged | 5 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#1 | Damaged | 1 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | nitrogen leak due to ruptured diaphram. | Completed 10/2/87 @ 0607. | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#1 | Undamaged | 6 | Transformer TR | TR2 | 0 | Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 14 | 0 | 0 | 0 | three phase, unit | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-23 | 0 | 0 | 0
SS#4 | Undamaged | 17 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse and ITE | 2300SF15000/20000-25 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#4 | Damaged | 1 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse | 2300SF15000/20000-30 | 0 | 0 | 0 | not known | to be replaced | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#4 | Undamaged | 18 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Allis Chalmers | oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#4 | Damaged | 5 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | functional immediately after eq, EPRI report indicates all had leaking seals | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#4 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | porcelain column shattered | to be rebuilt | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#4 | Undamaged | 84 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | frame mounted | 0 | 0 | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#4 | Undamaged | 12 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#4 | Undamaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | 3 o spare | 0 | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | 0 | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#4 | Undamaged | 6 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | Allis Chalmers | 1-0140-24784-1,-3;2-0102-9162-3, 7 | 0 | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | 0 | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#4 | Undamaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | General Electric | 3o D572975 | 0 | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | 0 | 0 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#4 | Damaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | Pennsylvania | 3o 01823-5-1 | 0 | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | Leaking 230 kV bushings. 2 or 3 bushings | Replaced "O" rings. Restored 11/2/87 @ 1630 | Quaternary formation - soft alluvium | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | Leak in non-CT column | Completed 10/3/87 @ 0227 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | Leak in non-CT column | Completed 10/4/87 @ 1654 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB4 | 0 | Written summary list ATB4 but data sheet gives W +M | 0 | 1 CT column | Completed 10/6/87 @ 2100. Note that repair was done after aftershock. | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | Leaks in CT columns | 0 | Quaternary formation - soil | 0 | No | 0 | 291.235 | 1991-12-08 | 0 | 0 | 0
SS#6 | Damaged | 2 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | Leaks in CT columns | Completed 10/3/87 @ 0227 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#6 | Undamaged | 10 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB4 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#6 | Damaged | 3 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB4 230-20000-6Y20 | 0 | Written summary list ATB4 but data sheet suggests ATB6 | 0 | Leak in 2 non-CT column and 3 CT columns | Completed 10/6/87 @ 2100. Note that repair was done after aftershock. | Quaternary formation - soil | 0 | No | 0 | 239 | 1991-12-08 | 0 | 0 | 0
SS#6 | Undamaged | 11 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB4 230-20000-6Y20 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#6 | Undamaged | 66 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#6 | Undamaged | 9 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#6 | Undamaged | 3 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | General Electric | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 6 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 12 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | oil | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 42 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 7 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#8 | Undamaged | 7 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#10 | Damaged | 1 | Circuit Breaker CB | CB | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | What type of equipment | 0 | Topping up needed but no leak found suggests that there was a leak that was self healing | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#10 | Undamaged | 6 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#10 | Undamaged | 12 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#10 | Undamaged | 6 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#10 | Undamaged | 6 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | General Electric | ATB 4-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#10 | Undamaged | 66 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#10 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#10 | Undamaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 66 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#15 | Undamaged | 12 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#15 | Undamaged | 30 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#15 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#15 | Undamaged | 6 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#16 | Damaged | 1 | Circuit Breaker CB | CB | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | Are there 66 kV SF6 CBs? | 0 | Ruptured releif valve | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#16 | Damaged | 1 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | non-CT columns leaking. crcked insulator. | 17 week lead time. | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#16 | Damaged | 2 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | 2 non-CT columns leaking. | complete 10/2/87 @ 2327 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#16 | Damaged | 2 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | 2 non-CT columns leaking. | complete 10/2/87 @ 1601 | Quaternary formation - soil | 0 | Yes | 0 | 247 | 1991-12-08 | 0 | 0 | 0
SS#16 | Undamaged | 10 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | 0 | 0 | There may be others that are not damaged. | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#16 | Undamaged | 12 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#16 | Undamaged | 12 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#16 | Undamaged | 78 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#16 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#16 | Undamaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#17 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Topping up needed but no leak found suggests that there was a leak that was self healing | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#17 | Undamaged | 36 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#17 | Undamaged | 23 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB 4-6 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#17 | Undamaged | 120 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#17 | Undamaged | 9 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#17 | Undamaged | 1 | Transformer TR | TR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | Not sure of voltage | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#17 | Damaged | 2 | Transformer TR | TR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | Not sure of voltages | 0 | Chipped bushing | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#17 | Undamaged | 3 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#19 | Damaged | 3 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB4 230-20000-0-20? | 0 | Note model no. indicated as Westinghouse. | 0 | 2 interrupter head bushings leaking, 1 CT and 1 non 0CT columns leaking. | repairs 60% complete 10/5/87. Note that repairs were not colpleted until after the aftershock. | soft alluvium - Quaternary formation | 0 | Yes | 0 | 245 | 1991-12-08 | 0 | 0 | 0
SS#19 | Undamaged | 39 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF6 | 0 | 0 | 0 | 0 | 0 | soft alluvium - Quaternary formation | 0 | Yes | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#19 | Undamaged | 3 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | oil | 0 | 0 | 0 | 0 | 0 | soft alluvium - Quaternary formation | 0 | Yes | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#19 | Undamaged | 3 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB4 230-20000-0-20? | 0 | 0 | 0 | 0 | 0 | soft alluvium - Quaternary formation | 0 | Yes | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#19 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | soft alluvium - Quaternary formation | 0 | Yes | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#19 | Undamaged | 102 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Low Design - Horizontal | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | soft alluvium - Quaternary formation | 0 | Yes | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#19 | Undamaged | 6 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | 0 | 0 | soft alluvium - Quaternary formation | 0 | Yes | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#19 | Undamaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | soft alluvium - Quaternary formation | 0 | Yes | 0 | 0 | 1998-07-01 | 0 | 0 | 0
SS#22 | Damaged | 2 | Circuit Breaker CB | CB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | What type of CB? | 0 | Cracked 66 kV bushing. | 0 | Quaternary formation - soil | 0 | No | 0 | 212 | 1991-12-08 | 0 | 0 | 0
SS#23 | Undamaged | 36 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse | 2300SF15000/20000-25 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#23 | Damaged | 1 | Circuit Breaker CB | CB9 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | leaking support column gasket. How many phases out? | Three days 14 hrs to repair | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#23 | Damaged | 1 | Circuit Breaker CB | CB9 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. | Quaternary formation - firm soil | 0 | No | 0 | 189 | 1991-12-08 | 0 | 0 | 0
SS#23 | Damaged | 1 | Circuit Breaker CB | CB9 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#23 | Damaged | 1 | Circuit Breaker CB | CB9 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#23 | Damaged | 17 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | functional immediately after earthquake, EPRI report indicates that all CBs eventually developed leaks | 0 | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#23 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. Restored 10/4/87 @ 0330 | Quaternary formation - firm soil | 0 | No | 0 | 186 | 1991-12-08 | 0 | 0 | 0
SS#23 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#23 | Damaged | 1 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | leaking support column gasket. How many phases out? | Three days 10 hrs to repair. | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#23 | Undamaged | 120 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | frame mounted | 0 | 0 | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1998-03-22 | 0 | 0 | 0
SS#23 | Damaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How was it installed? | Failed porcelain column | Can be restored by 10/10 (9 days) working 24 hr shift if part arrives. | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#23 | Undamaged | 5 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#23 | Undamaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | General Electric | 3o D582895, D596229 | 0 | 0 | Welded to embedded steel on mats | 0 | 0 | Quaternary formation - firm soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#27 | Undamaged | 1 | Capacitor Racks CR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How is it mounted? | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#29 | Undamaged | 1 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 post insulators for bus supports damaged. | Replaced 10/3/87 @ 2010 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#30 | Undamaged | 21 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Allis Chalmers | oil | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#30 | Undamaged | 48 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | frame mounted | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#30 | Undamaged | 10 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#30 | Undamaged | 4 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | Allis Chalmers | single phase | 0 | 0 | anchored by gussets welded to embedded steel | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#30 | Undamaged | 1 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | Westinghouse | 220000-072000 5066610 | 0 | 0 | anchored by gussets welded to embedded steel | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#30 | Damaged | 2 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | Westinghouse | 220000-072000 506668, -9 | 0 | 0 | anchored by gussets welded to embedded steel | functional, oil leaks at radiator flange. | 0 | Quaternary formation - soil | 0 | Yes | 0 | 187 | 1991-12-08 | 0 | 0 | 0
SS#30 | Damaged | 3 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | Westinghouse | 220000-072000 5069946, -7, -8 | 0 | 0 | anchored by gussets welded to embedded steel | functional, oil leaks at radiator flange. | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#32 | Damaged | 1 | Lightning Arrester LA | LA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How is it mounted? | Failure of porcelain. What voltage. What is significance of "Painted Bushing Cap"? | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#32 | Undamaged | 0 | Lightning Arrester LA | LA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How is it mounted? | . What voltage. What is significance of "Painted Bushing Cap"? | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#42 | Damaged | 1 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fitting on transfer bus broke?, What voltage? | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#43 | Damaged | 1 | Transformer TR | TR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | What type of TR? | 0 | Leaking 66 kV bushing. | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#46 | Damaged | 1 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Need manufacturer | 0 | 0 | 0 | 0 | Leaking bushings | Can be restored by 10/3 23:55 (2 Days 16 hrs). 1200 amp bushing was used instead of 1600 amp bushing as spare was not available. | Quaternary formation - soil | 0 | No | 0 | 197 | 1991-12-08 | 0 | 0 | 0
SS#46 | Undamaged | 23 | Circuit Breaker CB | CB20A | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | oil | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#46 | Undamaged | 57 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#46 | Undamaged | 9 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | How were LA installed? | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#46 | Damaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | 0 | three phase | 0 | What type of TR: Radiator size and mounting, LA mounting, No. of Phases? | 0 | What was damage to bushings? | There was not disruption of service due to bushing damage. Was it repaired? | Quaternary formation - soil | 0 | No | 0 | 0 | 1991-12-08 | 0 | 0 | 0
SS#46 | Undamaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 60 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 1998-03-25 | 0 | 0 | 0
SS#3 | Damaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | The boom was moderate length and had small gussets to stiffen the boom-TR connection. | Installed on three porcelain standoffs. There was almost no slack between bushing and LA and between LA and bus support column. | Cracked at base. Hinge is consistent with pull on bus. | 0 | Quaternary formation - soil | 0 | No | 0 | 374 | 1998-09-09 | 0 | 0 | 0
SS#3 | Undamaged | 20 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | The boom was moderate length and had small gussets to stiffen the boom-TR connection. | Installed on three porcelain standoffs. There was almost no slack between bushing and LA and between LA and bus support column. | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 375 | 1998-09-09 | 0 | 0 | 0
SS#3 | Damaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Hitachi | 0 | 0 | 3-phase, Bushings mounted on top of tall cylinders. | 0 | Three of the six bushings leaked, were leaking and had to be removed to restore. One bushing had a hairline crack along its length. These are draw-type bushings and the cracked unit had a tight fit to the draw mechanism. | The three bushings that had shifted and were leaking were repaired in the bushing shop. | Quaternary formation - soil | 0 | No | 0 | 371 | 1998-09-10 | 0 | 0 | 0
SS#3 | Damaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse | 0 | 0 | 3 phase | 0 | The TR case, about 3-1/2' above base had a crack in a weld at a corner. | Using a center punch, metal was moved to close the crack. | Quaternary formation - soil | 0 | No | 0 | 373 | 1998-07-06 | 0 | 0 | 0
SS#3 | Undamaged | 3 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse | 0 | 0 | 3 phase | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 372 | 1998-09-09 | 0 | 0 | 0
SS#3 | Undamaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 3 phase | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-18 | 0 | 0 | 0
SS#31 | Damaged | 15 | Circuit Breaker CB | CB14 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB7 | 0 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Damaged | 0 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF-6 | 0 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Undamaged | 45 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | SF-6 | 0 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Damaged | 7 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB 4-6 | 0 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Undamaged | 2 | Circuit Breaker CB | CB9 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | General Electric | ATB 4-6 | 0 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Damaged | 19 | Current-Voltage Transformer | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#31 | Undamaged | 26 | Current-Voltage Transformer | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#31 | Damaged | 75 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | only required adjustment | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Damaged | 42 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | visibly damaged | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Damaged | 21 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | seriously damaged | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Damaged | 0 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | Low Seismic | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Undamaged | 6 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | Low Seismic | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#31 | Damaged | 0 | Wave Trap WT | WT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#31 | Undamaged | 13 | Wave Trap WT | WT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 0 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Mitsubishi | SF6 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 87 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Mitsubishi | SF6 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 14 | Current-Voltage Transformer | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 40 | Current-Voltage Transformer | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Current-Voltage Transformer | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | Bank H, A phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Current-Voltage Transformer | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | Banks G1 & G2, A phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Current-Voltage Transformer | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | Banks G1 & G2, B phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 3 | Current-Voltage Transformer | CC5 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | Bank H, C phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 2 columns failed at base, Damage caused by interaction from adjacent equipment, pull over by WT | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | Bank H, B phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 1 column failed at base, Damage caused by interaction from adjacent equipment, pulled over by WT | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | Bank H, A phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 2 columns failed at base, Damage caused by interaction from adjacent equipment, pulled over by WT | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | Banks G1 & G2, A phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | both tripods failed | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | Banks G1 & G2, B phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 1 tripod failed | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | Banks G1 & G2, C phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 1 tripod failed | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 0 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vertical Swing | 0 | Bank H | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 0 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | Banks G1 & G2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E22, phase B, C | 230 | 0 | 0 | 0 | Southern States | 0 | 0 | Center break, sine beat tested | heavily braced support | 1 column failed, see page 56 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E2A, phase A, C | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 1 column failed, see page 56 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E32, phase C | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E32, phase B | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 1 column failed, see page 56 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E41, phase C | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E51, phase C, B | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E51 phase A | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 1 column failed, see page 57 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E81 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E91, phase B ,C | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 2 column failed, see page 59 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E91, phase A | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 1 column failed, see page 59 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E122, phase B | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 1 column failed, see page 59 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 2 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E92, phase B, C | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 2 column failed, see page 59 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 10 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Southern States | 0 | 0 | Center break, sine beat tested | heavily braced support | See page 56 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 146 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#44 | Damaged | 17 | Circuit Switcher CS | CS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | direct communication from Rulon Fronk | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2003-03-31 | 0 | 0 | 0
SS#34 | Damaged | 1 | Lightning Arrester | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | Bank H, C phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Post Supported | Failure in porcelain | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Lightning Arrester | LA5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 1 | Lightning Arrester | LA5 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | Bank H, A phase | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Post supported | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 5 | Lightning Arrester | LA5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 0 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 6 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 12 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 34.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | direct communication from Rulon Fronk | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2003-03-31 | 0 | 0 | 0
SS#34 | Undamaged | 0 | Transformer TR | TR1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 34.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | direct communication from Rulon Fronk | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2003-03-31 | 0 | 0 | 0
SS#34 | Damaged | 9 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | 1 phase | 0 | 0 | 0 | direct communication from Rulon Fronk | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2003-03-31 | 0 | 0 | 0
SS#34 | Undamaged | 0 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | 1 phase | 0 | 0 | 0 | direct communication from Rulon Fronk | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2003-03-31 | 0 | 0 | 0
SS#34 | Damaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | Vertically Suspended | 0 | 0 | 0 | 0 | 0 | E32 phase A | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | failure of 1 post insulator restraint, see page 56 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | Vertically Suspended | 0 | 0 | 0 | 0 | 0 | E42 phase A | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | failure of post insulator restraints, see page 57 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | Vertically Suspended | 0 | 0 | 0 | 0 | 0 | E52 phase A | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | failure of post insulator restraints, see page 57 ASCE | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 8 | Wave Trap WT | WT1 | 0 | 0 | 0 | Vertically Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Failure of support post insulators | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Damaged | 3 | Wave Trap WT | WT2 | 0 | 0 | 0 | Vertically Suspended | 0 | 0 | 0 | 0 | 0 | Bank G1 & G2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Post restraint | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 4 | Wave Trap WT | WT1 | 0 | 0 | 0 | Vertically Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#34 | Undamaged | 3 | Wave Trap WT | WT2 | 0 | 0 | 0 | Vertically Suspended | 0 | 0 | 0 | 0 | 0 | Bank H | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Cable restraint | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 0 | Circuit Breaker CB | CB20A | Bulk Oil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 114 | Circuit Breaker CB | CB20A | Bulk Oil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 0 | Current-Voltage Transformer | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 27 | Current-Voltage Transformer | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 3 | Circuit Switcher CS | CS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Post insulators failed, base bolts stretched | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 3 | Circuit Switcher CS | CS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 1 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Post insulator failed | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 119 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 2 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Post insulators failed | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 4 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 3 | Lightning Arrester | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 18 | Lightning Arrester | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 3 | Lightning Arrester | LA5 | 0 | 0 | Post-supported | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Failed at based of column | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 0 | Lightning Arrester | LA5 | 0 | 0 | Post-supported | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 1 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 1 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 3 | Potential Trans. PT | PT5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 34.5 | 0 | 0 | 0 | 0 | 0 | 3 phase | 0 | Lost LAs | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 5 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 34.5 | 0 | 0 | 0 | 0 | 0 | 3 phase | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 0 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 6 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | 0 | 0 | single phase | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 0 | Wave Trap WT | WT2 | 0 | 0 | 0 | Suspended | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 3 | Wave Trap WT | WT2 | 0 | 0 | 0 | Suspended | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | All wave traps undamaged but restraint on one WT damaged | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | Supported on DS frame | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Post failed | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 4 | Wave Trap WT | WT1 | 0 | 0 | 0 | Supported on DS frame | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Damaged | 0 | Pothead | PH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#35 | Undamaged | 9 | Pothead | PH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | Yes | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#36 | Undamaged | 72 | Circuit Breaker CB | CB20A | Bulk Oil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Most units are anchored with bolts through skid frame. | Some units showed signs of distress in the anchore bolts, that is, chipped paint or bent bolts. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 339 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 8 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | on structure with WT | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Total number of CCVTs disagrees with number in TCLEE report page 61 | Note that these units are supported on a beam spanning 2 DS rather than on its own support sturcture. | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 343 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 14 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 344 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 2 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 345 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 6 | Potential Transformer PT | PT1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-21 | 0 | 0 | 0
SS#36 | Damaged | 1 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E1, Aphase | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | 0 | Both support columns failed. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 337 | 1998-05-06 | 0 | 0 | 0
SS#36 | Damaged | 4 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E1, A, B, C phase | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | Note that a rigid bus connects the Bus 1 and Bus 2 Positions. | All of these failures were to the column that is connected by rigid bus to the adjacent switch. Note that these switches are braced in the direction of the rigid bus connection. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 338 | 1998-05-06 | 0 | 0 | 0
SS#36 | Damaged | 1 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | E1, C phase | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. |  | Both support columns failed | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#36 | Damaged | 12 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | 0 | unknown failure mode | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#36 | Undamaged | 54 | Disconnect Switch DS | DS2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | 0 | Some of these units have been damaged, but their position is not known. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 336 | 1998-05-06 | 0 | 0 | 0
SS#36 | Damaged | 2 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | 2 LA failed at standoff | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#36 | Damaged | 1 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | 1 failed at base of LA. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#36 | Damaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All LA failed but it is not known if there are standoffs. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#36 | Damaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All LA failed but it is not known if there are standoffs. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#36 | Undamaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#36 | Damaged | 1 | Transformer TR | TR2 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank A | 230 | 34.5 | 0 | 0 | 0 | 3-phase | 0 | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | All high voltage bushings moved. 2 LA failed at standoff, 1 at base of LA. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 349 | 1998-05-06 | 0 | 0 | 0
SS#36 | Damaged | 1 | Transformer TR | TR2 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank B | 230 | 34.5 | 0 | 0 | 0 | 3-phase | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All high voltage bushings moved. Also leaks in low voltage bushings. All LA failed but it is not known if there are standoffs. Anchor bolts stretched. There was a oil leak but it is not known if it is just the bushings. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 350 | 1998-05-06 | 0 | 0 | 0
SS#36 | Damaged | 1 | Transformer TR | TR2 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank D | 230 | 34.5 | 0 | 0 | 0 | 3-phase | 0 | Schematic on page 66 of ASCE | LA bus connections not to bushings. | All high voltage bushings moved. 1 LA failed at standoff, 2 at base of LA. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 352 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 1 | Transformer TR | TR2 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank C | 230 | 34.5 | 0 | 0 | 0 | 3-phase | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | It is not known if there are standoffs. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 351 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | V. Dual Post | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS | Unit was tilting, but was functional. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 346 | 1998-05-06 | 0 | 0 | 0
SS#36 | Damaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | Unit had to be removed and replaced, but damage not known. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 347 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 2 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | Units tilted,but functional. | 0 | Tertiary formation - soft rock | 0 | No | 0 | 348 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | V. Dual Post | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 340 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 341 | 1998-05-06 | 0 | 0 | 0
SS#36 | Undamaged | 2 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | 0 | 0 | Tertiary formation - soft rock | 0 | No | 0 | 342 | 1998-05-06 | 0 | 0 | 0
SS#37 | Damaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 at standoff , 4 at arrester | 0 | 0 | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#37 | Undamaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | Post mounted | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#37 | Damaged | 2 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 34.5 | 0 | 0 | 0 | 3-phase | 0 | 0 | 0 | 6 Leaking 230 kVbushings, 6 LA failed | 0 | 0 | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#37 | Undamaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 34.5 | 0 | 0 | 0 | 3-phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#38 | Undamaged | 54 | Circuit Breaker CB | CB20A | Bulk Oil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 368 | 1998-05-09 | 0 | 0 | 0
SS#38 | Damaged | 2 | Potential Transformer PT | PT1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | There may be a slack problem in that there is a short flexible connection to a rigid bus that is supported by disconnect switch structures. Pot head support structure is also connected to the rigid bus. | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 361 | 1998-05-09 | 0 | 0 | 0
SS#38 | Undamaged | 15 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 360 | 1998-05-09 | 0 | 0 | 0
SS#38 | Undamaged | 3 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-11 | 0 | 0 | 0
SS#38 | Damaged | 33 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 1600 | 900 | ITE | Type DR-5 | 0 | 0 | 0 | These units had deformed operating mechanism that prevented their operation. None of the post insulators were damaged. | It took 2 days to identify the problem and the fix and 2 hour for each (3 phases) to make repairs after that. | Quaternary formation - soil | 0 | No | 0 | 353 | 1998-06-10 | 0 | 0 | 0
SS#38 | Damaged | 24 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 1600 | 900 | ITE | Type DR-5 | 0 | 0 | 0 | These units had deformed operating mechanisms that prevented their operation. None of the post insulators were damaged. | It took 2 days to identify the problem and the fix and 2 hour for each (3 phases) to make repairs after that. | Quaternary formation - soil | 0 | No | 0 | 369 | 1998-06-10 | 0 | 0 | 0
SS#38 | Damaged | 6 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | 0 | 0 | unknown damage | Post insulators used for bus supports in PE4,5,6 were canibalized to reconstruct DS. | Quaternary formation - soil | 0 | No | 0 | 354 | 1998-06-10 | 0 | 0 | 0
SS#38 | Damaged | 6 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | 0 | rigid bus connection | One of the columns failed. 10 were adjacent to CB and were provided with good slack so that inertial loads were probably the cause of failure. One unit was connected to a bus with an intermediate drop and bus dynamics may have contributed to failure | Post insulators used for bus supports in PE4,5,6 were canibalized to reconstruct DS. | Quaternary formation - soil | 0 | No | 0 | 355 | 1998-06-10 | 0 | 0 | 0
SS#38 | Damaged | 13 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | 0 | rigid bus connection | Both columns failed. Interaction between columns may have contributed to the dual failures. . | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#38 | Undamaged | 23 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#38 | Damaged | 5 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | 1 column failed | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#38 | Damaged | 3 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | both columns failed | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#38 | Undamaged | 4 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#38 | Damaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | Frame | 0 | 0 | 0 | 0 | 0 | 0 | TR Bank B & C | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Standoffs failed | Standoffs failed | 0 | Quaternary formation - soil | 0 | No | 0 | 364 | 1998-05-09 | 0 | 0 | 0
SS#38 | Damaged | 2 | Lightning Arrester LA | LA1 | 0 | 0 | Frame- Pothead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unusual installation in that frame is much lower than that used for TRs. LA are on standoffs. There is marginal slack to a rigid bus that is supported on disconnect switches. | Standoffs failed | 0 | Quaternary formation - soil | 0 | No | 0 | 365 | 1998-05-09 | 0 | 0 | 0
SS#38 | Damaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | TR Bank E | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No Standoffs | Failed at base of LA | 0 | Quaternary formation - soil | 0 | No | 0 | 367 | 1998-05-09 | 0 | 0 | 0
SS#38 | Undamaged | 3 | Lightning Arrester LA | LA1 | 0 | 0 | Free Standing | 0 | 0 | 0 | 0 | 0 | 0 | TR Bank A | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 363 | 1998-05-09 | 0 | 0 | 0
SS#38 | Undamaged | 7 | Lightning Arrester LA | LA1 | 0 | 0 | Frame- Pothead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unusual installation in that frame is much lower than that used for TRs. LA are on standoffs. There is marginal slack to a rigid bus that is supported on disconnect switches. | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 366 | 1998-05-09 | 0 | 0 | 0
SS#38 | Damaged | 1 | Transformer TR | TR1 | 0 | Separate Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank B | 230 | 34.5 | 0 | 0 | 0 | 0 | 0 | TR in accountic enclosure. Separately supported radiators. Conservator tank with 2 supports. LA supported on frame with standoffs. | Ao and Co LA drops from bus, Bo from bushing. see page 71 ASCE | Bo Bushing has damaged bus stud. All LA failed, A & C at standoffs and B at LA base. Conservator stretched bolts and shifted in slotted connections, strain piping and lost all 1000g oil. | 0 | Quaternary formation - soil | 0 | No | 0 | 357 | 1998-06-10 | 0 | 0 | 0
SS#38 | Damaged | 1 | Transformer TR | TR1 | 0 | Separate Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank C | 230 | 34.5 | 0 | 0 | 0 | 0 | 0 | TR in accountic enclosure. Separately supported radiators. Conservator on 2 supports above TR. LA supported on frame. . | All LA have bus drops from bus. | All failed at standoffs and were not damaged. Signs of oil leak (spray on conservator) but source could not be found. | 0 | Quaternary formation - soil | 0 | No | 0 | 358 | 1998-06-10 | 0 | 0 | 0
SS#38 | Undamaged | 1 | Transformer TR | TR1 | 0 | Separate Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank A | 230 | 34.5 | 0 | 0 | 0 | 0 | 0 | TR in accountic enclosure. Separately supported radiators, which were moderately large. Conservator on top of radiators. LA supported on independent posts without standoffs. | LA drops from bus. | Signs of oil leak at valve inside of enclosure, but it looks old. | 0 | Quaternary formation - soil | 0 | No | 0 | 356 | 1998-06-10 | 0 | 0 | 0
SS#38 | Undamaged | 1 | Transformer TR | TR1 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank E | 230 | 138 | 0 | 0 | 0 | 0 | 0 | LA on boom without standoffs. High voltage LA have drops from bus. see page 71 ASCE | Unit anchored with gusseted angle to pull tabs. | 230 KV LA failed. They were boom mounted without standoffs. Small radiators. Flexible end anchors to pull tabs contributed to failure of bolted angles along side. | 0 | Quaternary formation - soil | 0 | No | 0 | 359 | 1998-06-10 | 0 | 0 | 0
SS#38 | Damaged | 3 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | These units have marginal slack. | 1 WT w/ failed posts at lower sand ring, 2 failed welds at top of posts connecting to wave trap support channel. | Two units were restored by bolting angles between channel and post cap. | Quaternary formation - soil | 0 | No | 0 | 362 | 1998-05-09 | 0 | 0 | 0
SS#38 | Undamaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 370 | 1998-06-10 | 0 | 0 | 0
SS#38 | Undamaged | 9 | Pothead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#41 | Undamaged | 6 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal - Low Design | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#41 | Undamaged | 6 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#41 | Damaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | radiator leak | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#41 | Undamaged | 1 | Transformer TR | TR2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 66 | 0 | 0 | 0 | three phase | 0 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#44 | Undamaged | 12 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghous-Mitsubishi Power Breaker | 200-SFMT-63B | 0 | 0 | Has very good slack to DSs. Pict 1-35 | E91 A had a loose bolt at south east corner. | 0 | Quaternary formation - soil | 0 | No | 0 | 320 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 45 | Circuit Breaker CB | CB20A | Bulk Oil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Siemens-Allis & ITE | 0 | 1983 & 1971 | 0 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-06-17 | 0 | 0 | 0
SS#44 | Damaged | 2 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | GE | 4CD3 | 0 | Installed on 6-3/4" diameter 8'-6" tall | Good slack in bus connection | A failed at lower sand ring and B did not look damaged on original trip. Unit was removed and porcelain was fractured 1/3 of the way up from base. Ao is would be inertial loads. Pict 3-34, 28-36 | 0 | Quaternary formation - soil | 675 | No | 0 | 319 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 1 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | GE | 0 | 0 | 0 | Units are on pedestals 6-3/4" diameter and 8'-6" tall | This unit was found removed 3/15/94. Pict 28-34 | 0 | Quaternary formation - soil | 0 | No | 0 | 332 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 8 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | GE | 4CD3... | 0 | Units are on pedestals 6-3/4" diameter and 8'-6" tall | Good slack in bus connection. Pict 2-15 | 0 | 0 | Quaternary formation - soil | 675 | No | 0 | 317 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 10 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | GE | 4CD3... | 0 | Supported on 6-3/4" 8'-6" tall | Good slack in bus connection. Pict 24-8 | 0 | 0 | Quaternary formation - soil | 675 | No | 0 | 318 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 2 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | A is Nisson Denki, B & C are GE. Pict. 24-4 | A & C have Bellville washers, B does not? | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 315 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 6 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Haeffey | 0 | 0 | mounted on 12" diameter post that is 7' high. Can is sealed in unusual way. Support post has 8 large gussets at base and top. Pict. 1-30, 28, 26, 25, 28-23, 22, 21 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 316 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 4 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse | 0 | 0 | Units have bellville washers. Support column is 13" diameter and 7'-8" tall. pict 28-27 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 333 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 3 | Coupling Voltage Trans. CVT | CC1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Trench | 0 | 0 | Support column is 13" diameter and 7'-8" tall all connected to a large metal base. Pict 28-34 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 334 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 4 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Southern States | 0 | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. | 0 | Support shaft failed so that it looked like a fatigue failure. Similar failure at RS E. Orientation of fractures are not consistant with position of arm. 92CL Pict 1-29,28,27,26,25. 101BL Pict1-21,20. 101BB Pict1-18,17,16,15. 91AB Pict 1-14. 28-24. Bus | 0 | Quaternary formation - soil | 0 | No | 0 | 312 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Southern States | 0 | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. | 0 | Porcelain failure at base. Fracture surface (hinge) suggests that it failed due to a pull by the bus. There were two failures adjacent to line drop. Pict 1-24,23,22,12,11. 28-24. Bus drop 1-34 indicated that swing at top of drop may have lifted drop. | 0 | Quaternary formation - soil | 0 | No | 0 | 313 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 15 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | Units supported on two columns | 0 | All failed at the base of the porcelain. Only one column failed. column E82CLB, E82ALB, E83Ab1b1, E83Ab2b1, E81CLL, E72BLL, E7Cb2b2, E73Bb2b2, E73Ab2b1, E71CBL, E71ALB, Bank F 230 Bank, Bank F 230 Bbank, Bank F 220 BB, Pict 1-8, 1-7,2-37, 2-18 | 0 | Quaternary formation - soil | 0 | No | 0 | 322 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 3 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | Units supported on two columns | 0 | Post insulators failed at sand ring. Both insulators failed. Pict 1-8 | 0 | Quaternary formation - soil | 0 | No | 0 | 323 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | Units supported on two columns. Pict 28-32, 31 | 0 | Post insulators failed at sand ring. | 0 | Quaternary formation - soil | 0 | No | 0 | 335 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 18 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Southern States | 0 | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. Pict 1-36 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 311 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 1 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Southern States | 0 | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 0 | 2002-07-19 | 0 | 0 | 0
SS#44 | Undamaged | 83 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Horizontal Swing | 0 | 0 | 230 | 0 | 0 | 0 | Cole | 0 | 0 | Units supported on two columns. 8-1/2" x 5" with about 3/8" wall with long direction in line with closed arm. Pict 28-31 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 321 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 12 | Lightning Arrester LA | LA1 | 0 | 0 | TR Boom Mount | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Pict 28-32, 2-13 | on porcelain standoffs, Support plates look thin. | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 329 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 4 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Support post is 6-3/4"diameter and 7'-10" high. Pict 3-38, 37,36,35,,33,32. | Units had Bellville washers. The base has small gussets. | Units all failed at the sand ring at base, except 230 Bus 2 A where damage was not obvious, but must have been it cracked. It did not have oil spill below it. Note that bus 2 side anchore bolts were streched and one was loose. On Bus 1 A & C o had st | 0 | Quaternary formation - soil | 0 | No | 0 | 310 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 6 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | Westinghouse | 0 | 0 | Support columns is very large with gussets at top but not at base. Support column is 15" Square and 7'-4" tall from top of lower support to bottom of top support. Pict. 1-37,15 | Units did not have Bellville washers. | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 309 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 2 | Potential Trans. PT | PT1 | 0 | 0 | 0 | 0 | Post Mounted | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | These units have much smaller section support column that 220 KV bus. Support post is 6-3/4"diameter and 7'-10" high. | Units had Bellville washers | Note that bus 2 side anchore bolts were streched and one was loose. On Bus 1 A & C o had streched bolts but were undamaged. Phase B did not strech but failed. Phase C gussett at base showed signs of distress. Pict 3-33 | 0 | Quaternary formation - soil | 0 | No | 0 | 314 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 1 | Transformer TR | TR2 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank F | 230 | 220 | 0 | 0 | Westinghouse | 0 | 0 | 3 phase Auto transformer 220 to 230 KV | Radiators braced at the bottom | Weld to embedment failed. It was a poor weld and not much material was put down. The concrete was fractured where the embedment tried to pull out. The transformer moved about 14" to the north. Pict 2-10,, 9, 8, 7, 6, 28-32 | 0 | Quaternary formation - soil | 537000 | No | 0 | 331 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 1 | Transformer TR | TR2 | 0 | Small Rad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bank E | 230 | 220 | 0 | 0 | Westinghouse | 0 | 0 | 3 phase Pict 2-13 | Radiators braced at the bottom, welded to embedment | 0 | 0 | Quaternary formation - soil | 527000 | No | 0 | 330 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weld on one side channel failed. Other channel tore. Pict 2-35, 34, 33, 32, 29, 2-17 | 0 | Quaternary formation - soil | 0 | No | 0 | 328 | 1998-04-06 | 0 | 0 | 0
SS#44 | Damaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | V. Suspended | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Pict 24-6 | 0 | bolts failed on restraint, WT ok | 0 | Quaternary formation - soil | 0 | No | 0 | 324 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 2 | Wave Trap WT | WT1 | 0 | 0 | 0 | V. Suspended | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Pict 24-7, 8 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 325 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 1 | Wave Trap WT | WT1 | 0 | 0 | 0 | V. Post Mounted | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Units supported on three columns. Pict 24-4 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 326 | 1998-04-06 | 0 | 0 | 0
SS#44 | Undamaged | 2 | Wave Trap WT | WT1 | 0 | 0 | 0 | H. Post-Insulator | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | Pict 28-29 | 0 | 0 | 0 | Quaternary formation - soil | 0 | No | 0 | 327 | 1998-04-06 | 0 | 0 | 0
SS#45 | Damaged | 1 | Circuit Breaker CB | CB15 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | General Electric | ATB | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 8 | Circuit Breaker CB | CB15 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | General Electric | ATB | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Damaged | 2 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Westinghouse | seismic | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 4 | Circuit Breaker CB | CB72s | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Westinghouse | seismic | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 33 | Circuit Breaker CB | CB20 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 21 | Circuit Breaker CB | CB57 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | Siemans | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 9 | Circuit Breaker CB | CB73 | Live Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | Westinghouse | Puffers | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 6 | Circuit Breaker CB | CB77 | Dead Tank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | SF-6 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Damaged | 2 | Current Transformer CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | Low Seismic | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | broken | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 24 | Current Transformer CT | CT1 | 0 | 0 | 0 | 0 | 0 | 0 | Low Seismic | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 13 | Current Transformer CT | CT5 | 0 | 0 | 0 | 0 | 0 | 0 | Low Seismic | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Damaged | 21 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Low Design | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 45 | Disconnect Switch DS | DS1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Low Design | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 108 | Disconnect Switch DS | DS3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Low Design | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 10 | Lightning Arrester LA | LA1 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Damaged | 7 | Lightning Arrester LA | LA5 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 21 | Lightning Arrester LA | LA5 | 0 | 0 | Low Design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Damaged | 3 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | single phase | 0 | composite bushing | 0 | radiator leaks | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 7 | Transformer TR | TR3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 230 | 0 | 0 | 0 | single phase | 0 | composite bushing | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-04-03 | 0 | 0 | 0
SS#45 | Undamaged | 10 | Wave Trap WT | WT2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | Suspended | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#45 | Undamaged | 60 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-07-09 | 0 | 0 | 0
SS#45 | Damaged | 4 | Bus Support | BS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mesozoic formation - hard rock | 0 | Yes | 0 | 0 | 2002-07-09 | 0 | 0 | 0

## Comments
MANUFACTUR | MODEL_DES | EQP_COMMENT | EQP_INSTAL | EQP_DAMAGE | RESTORATION
0 | SF6 | 0 | 0 | SF6 leaking at entrance bushing on non-CT column. Is this support column or bushing? What type of equipment. | 0
0 | 0 | What type of equipment | 0 | 0 | 0
0 | 0 | 0 | 0 | What was problem? | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | Cracked non-CT support column. | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
General Electric | 3o D572975 | 0 | 0 | Oil leak. Where? Which unit? | 0
Pennsylvania | 3 phase | 0 | 0 | Gas leak in man hole cover. Which unit? | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | Blown seals on bushing #2. What is bushing #2. This is probably inner interrupter head bushing. what phases? | restored 10/5/87 @ 2300
General Electric | ATB5 230-20000-5-20 | 0 | 0 | There is also another ATB 4 or 6 | 0
General Electric | 0 | 0 | 0 | This data added to reflect total of 30 at site | 0
0 | 0 | 0 | 0 | Failed porcelain. How was it mounted. | 0
0 | 0 | 0 | 0 | How was it mounted. | 0
0 | 0 | Equipment info not provided | 0 | Top plate gasket leaking. | 0
0 | 0 | 0 | 0 | Oil leak | 0
0 | 0 | 0 | 0 | Chipped bushings. Need details. | 0
0 | 0 | Voltage and type not known | 0 | What was problem? | 0
0 | 0 | 0 | 0 | Burnt. Is this contacts? | 0
General Electric | ATB-550-2 SN 0139A8759-204 | 0.2 g static seismic specification | 0 | Gasket leak at base of top porelain member above CT lead. | 2 days to repair. No effect on service.
General Electric | ATB-550-2 | 0.2 g static seismic specification | 0 | 0 | 0
0 | Oil | 0 | 0 | 0 | 0
0 | unknown | 0 | 0 | 0 | 0
Westinghouse | ? 2 head, | 0 | 0 | 0 | 0
0 | 0 | 0 | Installation not verified. Associated with 500/230 kV TR Bank 11. | Failed porcelain | replaced
0 | 0 | 0 | Installation not verified. Associated with 500/230 kV TR. | 0 | 0
Westinghouse | single phase | 0 | 0 | 0 | 0
General Electric | K 546561 thru 64, auto, ccoled by OA/FA/FOA | 0 | 0 | all 500 kV bushings shifted 3/8". leaking oil | 20 days to repair. No effect on service.
0 | oil | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | out of adjustment | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | three phase, step up | 0 | 0 | radiator leak | fixed using wrench to tighten bolts
0 | three phase, step up | 0 | 0 | 0 | 0
Westinghouse | 3200y SF15000/20000 sn2-62y1128 | 0 | 0 | 0 | 0
0 | Oil | 0 | 0 | 0 | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, flexible loop bus connection to CT | All three interrupter head support columns failed. Adjacent CT and DSW did not fail. Support structure moved from under friction clips North about 1 foot. | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Center interrupter head support column failed. Entire column failed. Adjacent CT and DSW did not fail. | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Interrupter head support column near disconnect switch failed. Upper part of column failed. Adjacent CT and DSW did not fail. | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT | Interrupter head support column near disconnect switch failed. Upper part of column failed. Entire column near CT failed. Adjacent CT and DSW did not fail. | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit tipped over, flexible loop bus connection to CT. | All interrupter head support columns failed. Entire column near CT failed. Adjacent CT did not fail. Adjacent DSW did fail. Support structure moved about 6" from under friction clips. | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | Interrupter head support column near disconnect switch failed. The entire column failed. Adjacent CT and DSW did not fail. No significant displacement of support structure. | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | All interrupter head support columns failed. The entire column failed. Adjacent CT and DSW did not fail. | 0
Westinghouse | SF6, Seismic, modified 1973 | Seismically strengthen with fiber glass tendons. | Friction clip anchors, unit did not move significantly, flexible loop bus connection to CT. | 0 | 0
0 | Unknown | it is unclear from documentation of this is a bulk oil or SF6 | 0 | 0 | 0
High Voltage Breaker, Inc.(Hitachi/Westinghouse) | H 550-40000-3 SN 5500A2012-203 | Bushings are attached to sand ring which is bolted to CB body, 2 cycle interrupt, shake table tested | 0 | 0 | 0
General Electric | ATB6 y | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Units had flexible loops connecting CT to CB | Some of the couplings between CT and CB may have broken | required removal of contaminated ground below each leaking CT.
0 | 0 | 0 | Units are mounted on Tit-tat-toe chair are are relatively flexible to rotation. Units had flexible loops connecting CT to CB | Oil leaks between bushing and tank. Some of the couplings between CT and CB may have broken | required removal of contaminated ground below each leaking CT.
0 | 0 | 0 | 0 | Failure of outside double post and top of inner double post. Probably due to failure of adjacent CB but taken as independent failure. | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Bus support structure, pin and cap insulators. | 0 | 0
0 | 0 | 0 | Ground support structure, pin and cap insulators. | 0 | 0
0 | 0 | 0 | Bus support structure, pin and cap insulators. | 0 | 0
0 | 0 | 0 | Ground support structure, pin and cap insulators | 0 | 0
0 | 0 | 0 | Mounted on 500/230 kV McGraw Edison TR. | 0 | 0
0 | 0 | 0 | mounted on 500/230 kV Westinghouse TRs. | 0 | 0
0 | 0 | 0 | Associated with 230/115 kV Pennsylvania TRs (Bank 1 &2). Mounted on long boom. | 0 | 0
0 | 0 | 0 | mounted on 500/230 kV General Electric TRs. One of these may have been damaged (see record 292) | One of these may have been damaged? | 0
Westinghouse | 0 | 0 | Associated with W 500/230 kV TR | Porcelain failure, but unit fell to ground indicating bus connection failure. TR record 67. Not sure if this was 500 or 230 kV LA that failed. | 0
0 | 0 | Note that the LA with the GE were composed of 4 identical sections while others had large and medium sections and a short support section. | Associated with GE 500/230 kV TRs ( at west end of site). | Unit at east end of row may have been damaged - See record 292 | 0
0 | 0 | Note that the LA with the GE were composed of 4 identical sections while these had large and medium sections and a short support section. | Associated with W 500/230 kV TRs and ME TR (east end of site). | Unit at east end of row may have been damaged - See record 292 | 0
0 | 0 | 0 | 0 | 0 | 0
Pennsylvania | Spec. 10035, sn 0-02265-5-3, | Rad. elements supported from tank. C&C 94700, T&F 64400, 6970 g - 54300. | 230 LA on boom, 115 LA on rad. | 0 | 0
Westinghouse | OA, FA, FO, Core type. | Large radiators with each element supported from a TR tank. Rad. on sides and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 4 th from east end - use as spare. 230 LA on boom. 500 LA on independent latus structure. Units 1, 2 and 4 from east end of site. Welded to embedment | 0 | put into service when McGraw Edison units has bushing leak.
McGraw Edison | Spec. 13330, sn C06503-5-7, HV bushing no. 501.LL.716 | Large radiators with each element supported from maniford perp. to TR tank. 70" X 127" along TR. They are supported on non-penatrating pipe at bottom and penetrating pipe at top. There are horizontal braces at bottom but not consistant (one brace was | 230 LA on rad., Welded to embedment | The 500 kV bushing shifted about 1/4" and had an oil leak at the steel/porcelain interface. Bushing was bottom attachment type rather than draw out type. Were was leak, at bushing-flange or flange -tank? | The replacement bushing is 153" from flange to top and 76" from flang down.
Westinghouse | OA, FA, FO, Core type. | Large radiators with each element supported from a TR tank. Rad. on sides and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 230 LA on boom. 500 LA on independent latus structure. Units 1, 2 and 4 from east end of site., Welded to embedment | Minor oil leaks on B phase. note that A phase (east unit) lost LA, original slides indicated minor leaks at radiators (see record 292) Operational | 0
General Electric | OA, FA, FO, sn D577035, -6, 7, HV bushing no. 11B775, LV bushing no. 11B765 | 2 large radiators per side with each element supported from heavy box beam perp. to TR body and with non-penatrating connection with gusset plates for vert. load. Top connection is penetratng pipe. Each 142" long. There are diagonal braces at bottom, | West end of TR row. 230 kV LA installed on rad. | Severe oil leaks at the upper flange connection of manifold to tank. Flanges were deformed and peening was required to stop leaking. Repairs were made without the need to removed radiators or manifold. | Units were out for several days? Extensive excavation to removal contaminated soil.
0 | 0 | Wave trap size is about 4 feet in diameter and 6 feet long | mounted on support with CVT | 0 | 0
0 | 0 | Wave trap size is about 2 feet in diameter and 4 feet long | mounted on support with CVT | 0 | 0
0 | 0 | 0 | mounted on support with CVT | 0 | 0
0 | Oil | 0 | 0 | 0 | 0
BBC | 242PA4020 | A relatively new three phase CB was undamaged. | Welded anchorage into embedment | 0 | 0
BBC | 0 | A relatively new three phase CB was undamaged. | Welded anchorage into embedment | 0 | 0
Hitachi | HVB242-400001 | These were associated with Capacitor banks. | These were located on a new site adjacent to and north of the 230 kV site. | 0 | 0
0 | 0 | 0 | Mounted on 2 legged lattice structure with WT | Porcelain failed at its base. | 0
0 | 0 | 0 | number of power mounted and structure/wt not known. | Total number at site not known.(it is known that there were a minimum of three) | 0
0 | 0 | 0 | mounted on tall frames | Bus connections to switches were misaligned. Impact on operation is not clear but EPRI report indicates that they would not operate properly. | 0
0 | 0 | 0 | Bus supported. | Bus connections to switches were misaligned. Impact on operation is not clear but I seem to call that they would not operate properly. | 0
0 | 0 | 0 | The LA was mounted on a long extension arm off of TR bank 4 & 4A | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. | 0
0 | 0 | 0 | The LA was mounted on a long extension arm off of TR bank 5 | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. | 0
0 | 0 | 0 | The LA was mounted on a long extension arm off of TR bank 4 & 4A | LA fractured at its base. It was supported by bus flexible bus and was connected to an adjacent bushing. The bushing had chipped sheds were the LA hit it. Bushing continued to operate. | 0
Westinghouse | 0 | 0 | 0 | Core damage | 0
McGraw Edison | 0 | 0 | this was spare. | 0 | 0
Westinghouse | 0 | 0 | Station power components were mounted on "pipe" framed structure. This may have contributed to bushing and LA damage. There was not much slack between porcelain and support structure. | Damage to tertiary 12 kV bushings to station power, | After replacement there was still problems. Lightning Arrester had to be removed. It is not clear if this impacted station operations or operation of TRs.
Westinghouse | 0 | 0 | 0 | Damaged LA swung and chip shed on bushng or LA | After replacement there was still problems. Lightning Arrester had to be removed. It is not clear if this impacted station operations or operation of TRs.
0 | 0 | 0 | Mounted on support with CCVT | It is unknown how many there are. There are at least three. | 0
0 | 0 | Transfer busses above TR banks | Transfer busses were support at top of bus support structure. Transfer busses were supported by pin and cap post insulators. | On each of two structures, post insulators failed. In one case it dropped the bus across flexible bus connected to the bus support structure. In one case a bell on a bus string was damaged and was replaced. | 0
0 | 0 | Bulk oil type CB. | 0 | 0 | 0
0 | 0 | Bulk oil type CB. | 0 | Sheds on bushing chipped due to failure of switch above CB. | 0
Westinghouse | SF6, Seismically Strengthened 1973 | 0 | Units anchored with unwelded, single bolt friction clips. Rigid link between CB and CT. l | Failure of one support column next to CT. | 0
Westinghouse | SF6, Seismically Strengthened 1973 | 0 | Units anchored with unwelded, single bolt friction clips. Rigid link between CB and CT. | Failure of one support column next to DS. | 0
Westinghouse | SF6, Seismically Strengthened 1973 | 0 | Units anchored with unwelded, single bolt friction clips. Nine of the 12 units had flexible links between CB and CT, three had rigid links (522). | One phase toppled from slab, others moved, did not move or did not move significantly. Details of damage to specific units were difficult to determine from pictures. | 0
High Voltage Breaker, Inc. | HVB-550-400000-0, sn550A2009-205 | Bushing has flange bolted to CB body. | Units anchored with about a foot of weld (only one side could be seen in picture) to a cast in place embedment. | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | These were adjacent to dead-tank CB. | 0 | 0
0 | 0 | 0 | Mounted on lattice structure with WT. Two may not have had WTs. Units after they were repaired or replaced: 5 GE with 3 porcelain segments and 1 (WE?) with 4 porcelain segments. | 0 | 0
0 | 0 | 0 | Units had flexible connects to CB. Units held with friction clips. Support structure very flexible. | 0 | 0
0 | 0 | 0 | Units had rigid connects to CB. Units held with friction clips. Support structure very flexible. | Porcelain failed near top. | 0
0 | 0 | 0 | Units had flexible connects to CB. Units held with friction clips. Support structure very flexible. | Ceramic failed near top in most cases. In one case it failed about middle. One unit toppled from pad. Some failures may be due to secondary damage when CB failed. Bus connections to CB on several units fail at CB side, presumably after porcelain fai | 0
0 | 0 | 0 | 0 | damage unkown | 0
0 | 0 | 0 | 0 | Just the post insulator on the contact side failed. It was connected to the bus that fell. | 0
0 | 0 | 0 | 0 | unit adjacent to the dead tank CB had the blade misaligned. It is not know if it was functional. | 0
Southern States | 0 | 0 | 0 | The insulator on the contact side had bolts fail at base of post. Inadequate thread penetration. | 0
0 | 0 | 0 | 0 | One or both of the post insulators on the hinge side failed and the post insulator in the contact side also failed. | 0
0 | 0 | 0 | 0 | One or both of the post insulators on the hinge side failed and the post insulator in the contact side did not fail. | 0
0 | 0 | 0 | 0 | One or both of the post insulators on the hinge side failed and the post insulator in the contact side did not fail. | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Bus supported. | 0 | 0
0 | 0 | 0 | Bus supported. | 0 | 0
0 | 0 | 0 | Bus supported, bus sectioning switch. | It appears these DS were pulled apart by the out of phase dynamic response of adjacent bus sections | 0
0 | 0 | 0 | Bus supported , bus sectioning switch. | 0 | 0
0 | 0 | 0 | Bus supported. | 0 | 0
0 | 0 | 0 | Bus supported. | 0 | 0
0 | 0 | 0 | Supported on its own structure. | Not sure if any of these were damaged. | 0
0 | 0 | 0 | Mounted on radiator of 500/230 kV TR, Bank 9. | 0 | 0
0 | 0 | 0 | Mounted on 230/115 kV Bank 8. It is mounted on radiator. | 0 | 0
0 | 0 | 0 | Lattice-type post support. Adjacent to 500/230 kV TR, Bank 9. | 0 | 0
General Electric | 0 | 0 | 0 | 0 | 0
General Electric | 0 | 0 | 0 | 0 | 0
McGraw Edison | OA, FOA, FOA, sn C04169-5-2 | 11270 g of oil with wt of 84500, rad stick out 66", have large rad supports and relatively small rad. There is tertiary 13200 winding. Each TR has 5 bushings. Tertiary bus looks very flexible and there is little slack to bushings and LA. Note TR for | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts.
McGraw Edison | OA, FOA, FOA, sn C04169-5-2 | 11270 g of oil with wt of 84500, rad stick out 66", have large rad supports and relatively small rad. There is tertiary 13200 winding. Each TR has 5 bushings. Tertiary bus looks very flexible and there is little slack to bushings and LA. Note TR for | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts.
McGraw Edison | Spec. 13135-A, sn C05322--5-1 (single phase) | Rad. are are mounted on 3 sides, each with large box beam perp. to TR body with 4 rad. cores on each side of beam. Over all rad. is 68" out and 138" along TR. Lower rad support is large box beam that has no diagonal bracing but there are horizontal supp | anchored by welding to embedment | Minor oil leaks. | No impact on service. They may have been repaired by tightening bolts.
Westinghouse | FO, FA, three phase | 8020 g . TR is tall with small foot print. (about 13' x 13'). While rad are not very heavy, upper penetration supports total weight. | anchored by welding to embedment but angles are bolted to TR with what looks like small bolts. | original pictures indicate that one had small oil leak at rad. | No impact on service. They may have been repaired by tightening bolts.
McGraw Edison | 0 | 0 | 0 | 0 | 0
0 | 0 | Each WT is about 2' in diameter and 2' long. | Mounted on structure with CVT | 0 | 0
0 | 0 | Each WT is about 2' in diameter and 3' long. | Mounted on structure with CVT | 0 | 0
0 | 0 | Each WT is about 3' in diameter and 5' long. Insulators are tapered. | Mounted on lattice structure with CVT | porcelain supports failed | 0
0 | 0 | Each WT is about 3' in diameter and 5' long. Insulators are tapered. | Mounted on lattice structure with CVT | 0 | 0
0 | 0 | bus on site was 4 1/2 and 8 dia. al. pipe. West bus. Each bus has 6 insulator supports, each with 6 tapered sections. | 0 | All post insulators supporting B phase bus failed, dropping the bus. Connector between top of post insulator and bus may have been weak spot. Some units failed at connection and some had porcelain failure. This was bus B phase on west side of site. | 0
0 | 0 | East 3 phases of bus is 8". After earthquake there are 15 supports with 6 tapered elements, 7 with 2 elements, and 2 with 3 elements. | 0 | One insulator supporting one bus C on east side of site failed, the bus dropped but did not fall or malfunction. | 0
0 | 0 | West bus, A and C phase did not fail. Bus 8" diameter pipe, with 6 insulators per bus, each with 6 tapered sections. | 0 | 0 | 0
0 | 0 | East 3 phases of bus is 8". After earthquake there are 15 supports with 6 tapered elements, 7 with 2 elements, and 2 with 3 elements. 8 insulators per bus. | 0 | 0 | 0
General Electric | oil | 0 | 0 | 0 | 0
Westinghouse | oil | 0 | 0 | 0 | 0
Allis Chalmers | oil | 0 | 0 | 0 | 0
General Electric | ATB 4 or 6 | 0 | 0 | Support column gasket leaks. | 0
General Electric | ATB 4 or 6 | 0 | 0 | 0 | 0
General Electric | 0 | 0 | 0 | 0 | 0
Westinghouse | 0 | 0 | 0 | 0 | 0
Westinghouse | 0 | 0 | 0 | 0 | 0
General Electric | ATB7 | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | Air supply looked good. Lowest porcelain on CT support column failed. | 0
General Electric | ATB7 | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | 0 | 0
General Electric | ATB7, ATB-242-43000-7 | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | This equipment was only viewed after it was in bone yard, so specific equipment could not be associated with specific dispatch positions, and parts could not always be associated with a single phase. It is assumed that at least one support column usuall | 0
Westinghouse | Oil | Lattice type support structures were relatively tall, about 6', and appeared to be flexible in the longitudinal direction. Column natural frequencies of these CB are very low, about 1 or 2 Hz. | Units were well anchored with cast-in-place bolts at each of 4 corners of the two support columns. | This equipment was only viewed after it was in bone yard, so specific equipment could not be associated with specific dispatch positions, and parts could not always be associated with a single phase. It is assumed that at least one support column usuall | 0
General Electric | ATB 4 230-15000-4 | 0 | 0 | Do not have any details on damage of these units. | 0
0 | 0 | 0 | mounted on lattice structure that supported WT and CVT. | CVT porcelain column broke at base of column. | 0
0 | 0 | may be more than one | Mounted on lattice structure with WT. There was at least one other. | how many were undamaged, and what was installation. | 0
0 | 0 | The insulators were cap&pin type (Victor) | These units were supported high on the bus support structure, they were probably CB disconnect switches. They were mounted with the porcelain in the horizontal position. | There were two failures of post insulators. | 0
0 | 0 | 0 | 0 | There were one to three type of failures. In one, a weld that connects the base of the plate that is bolted to the bottom flange of the post insulator failed so that no torque could be applied to the column to change the position of the switch. There w | 0
0 | 0 | How many undamaged switches were there and how were they mounted? | 0 | 0 | 0
0 | 0 | The insulators were cap&pin type. | These units were supported high on the bus support structure, they were probably CB disconnect switches. They were mounted with the porcelain in the horizontal position. | 0 | 0
0 | 0 | 0 | Mounted on body of 230/115 kV McGraw Edison TR Bank 7 | 0 | 0
0 | 0 | 0 | Mounted on General Electric TR Banks 5 & 6. It is not clear how they are mounted - body or boom. | 0 | 0
0 | 0 | 0 | Seven TRs mounted on large elevated pads. Three mounted with bolts that were grouted in along sides of pad through large angle came lose. This was an old installation. The grout had the consistency of very weak plaster of Paris. | 0 | The was no impact of operations.
McGraw Edison | 0 | photo page 3-74 of EPRI NP-7500-SL | 0 | Replace seals at upper connection to stop leaking. Not sure how many leaks. I think there were 4 TRs. On return visit I thought that deformation of lower support was recorded but I could not find it in my slides. | Excavate to remove soil that had absorbed spilled oil.
General Electric | 0 | 0 | 0 | 0 | 0
0 | 0 | Section of rigid bus that passes over bus support structure and forms connection between flexible bus and CB had its end casting fail. | 0 | 0 | The fallen bus fell on flexible bus of three phases.
0 | 0 | Hook connection between strain bus and bus support structure became unhooked and dropped bus. | 0 | 0 | 0
0 | 0 | Transfer bus. | 0 | Post insulators supporting a section of transfer bus failed, allowing the bus to fall in one case or drop in another | The fallen bus fell on flexible bus of three phases.
0 | 0 | Transfer Bus | 0 | 0 | 0
0 | 0 | Section of rigid bus that that connects to flexible bus to by-pass CB on top of support structure had its end casting fail, allowing rigid bus to swing and come in contact with bus support structure. | 0 | 0 | The fallen bus fell on flexible bus of three phases.
0 | 0 | Synchronous Condenser. When I visited the site, it looked like one of the units was being worked on. There was a portable nitrogen supply connected to the units. There may have been a gas leak. | 0 | 0 | 0
S & C | 0 | Circuit switcher 115 kV | 0 | Blew up. | CB 112 relayed on fault pressure. There was not test made. Bank was inspected, looked OK and CB closed @ 1410. At 1425 117 blew up and CB 112 isolated station. Cleared 117 and picked up one bank.
Allis Chalmers | ABM SN 11714 | 0 | 0 | Aluminum casting that supports the interrupter head failed. | Out of service for 4 days - no effect on service.
Allis Chalmers | ABM SN 11714 | seismic specification was 0.2g static horizontal. | 0 | 0 | 0
Westinghouse | 2300SF1500 | 0 | 0 | 0 | 0
Pen | Oil, RHE90 | 0 | 0 | 0 | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications, original specifications was .2g horizontal - static | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | Interrupter head support column adjacent to CT failed - lowest ceramic member cracked. 4 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 2 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 0 | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | Cracked interrupter head support column adjacent to CT. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 0 | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 0 | 0
Westinghouse | SF6 500SF35000, SN Z 62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 1 damaged guy. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 6 hrs to repair guy at a convenient time.
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 3 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is very flexible. Both welded and friction clip anchorage. Installed in 1967. | 2 damaged guys. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is more rigid than x2x units. Both welded and friction clip anchorage. Installed in 1968. | 1 damaged guy - next to CT. It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0
Westinghouse | SF6 500SF35000, SN 3-62Y5007 | No Seismic modifications | Rigid connection between CB and CT, CT support is more rigid than x2x units. Both welded and friction clip anchorage. Installed in 1968. | It is not clear why so many more guys on 922, 822 and 722 failed relative to 942, 842, 742. While depth of fill was probably deeper on the X22 units, motion was described as periodic so it may be differences in frequency. | 0
General Eelctric | ATB 500380001K | 0 | 0 | 0 | 0
0 | Unknown | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | SF6 | 0 | 0 | 0 | 0
0 | Oil | 0 | 0 | 0 | 0
Westinghouse | SF6, 500SF35000,SN 3-62405041 Seis reinforced 1973 | Seismically strengthened 1973 by replacing wood tendons with fiberglass. Originally were 0.2g static horizontal. Note that SCE seismic units also have dampers. | Anchor bolts securing friction clips on 6 legs stretched or pulled out slightly. Adjacent current transformers had tit-tat-toe chair support that was flexible and there were signs of distress in cracked paint but no permanent deformations. Rigid connec | Interrupter head near CT failed explosively and with internal part of interrupter severely burned. There was not significant shifting of CB on its pad. There may have been vertical impact due to stretch or pullout of anchor bolts. Motion of CT may hav | 9 days to restore, did not cause disruption.
Westinghouse | SF6, 500SF35000,SN3-624-5041 Seis | Seismically strengthened 1973 by replacing wood tendons with fiberglass. Originally were 0.2g static horizontal. Note that SCE seismic units also have dampers. | Anchor bolts securing friction clips on 6 legs stretched or pulled out slightly. Adjacent current transformers had tit-tat-toe chair support that was flexible and there were signs of distress in cracked paint but no permanent deformations. Rigid connec | 0 | 0
0 | Unknown | 0 | 0 | 0 | 0
General Electric | ATB6 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Don't know how many but there are at least 6 | 0 | 0
General Electric 192 | 9L11AW736 Alugard | Pictures indicate that there was a short porcelain section at base with a coupling to a long upper section. | Mounted on boom on 230/115 Pennsylvania TR | The short lower porcelain member of LA that failed. | 6 hours to repair, no effect on operation at site
0 | 0 | Pictures indicate that there was a short porcelain section at base with a coupling to a long upper section. | Mounted on boom on 230/115 Pennsylvania TR | 0 | 0
0 | 0 | mounted on body of 500/230 kV TR | 0 | 0 | 0
0 | 0 | 0 | Associated with 500/230 kV TR | 0 | 0
Pennsylvania | Spec. 10035, sn 0-02265-5-3 | Rad. elements supported from tank. C&C 94700, T&F 64400, 6970 g - 54300. | 230 LA on boom, 115 LA on rad. | 0 | 0
Westinghouse | single phase | 0 | 0 | 0 | 0
McGraw Edison | Spec. 13330, sn C06503-5-7 | Large radiators with each element supported from maniford perp. to TR tank. 70" X 127" along TR. They are supported on non-penatrating pipe at bottom and penetrating pipe at top. There are horizontal braces at bottom but not consistant (one brace was | 230 LA on rad. | 0 | 0
General Electric | OA, FA, FO, sn D577035, -6, 7 | 2 large radiators per side with each element supported from heavy box beam perp. to TR body and with non-penatrating connection with gusset plates for vert. load. Top connection is penertatng pipe. Each 142" long. There are diagonal braces at bottom, | West end of TR row. 230 kV LA installed on rad. | 0 | 0
Westinghouse | OA, FA, FO, Core Type | Large radiators with each element supported from a TR tank. Rad. on sies and end. End rad has 9 sections and side has 5 with length 92". There are diagonal braces from top of TR to outside bottom of rad and is 1" rod - 5 on side rad and 3 on end. Ther | 230 LA on boom. 500 LA on independent lattice structure. Units 1, 2 and 4 from east end of site. | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | ITE "watch bob" gas type | 0 | 0 | 0
0 | 0 | vertical tank type oil circuit breakers | 0 | 0 | 0
Cogenel | air blast | flexible conductors, dynamic analysis 0.5 g PGA design specification | mounted on steel A-frame w/ horizontal pressure vessel, breaker head mounted on 30 ft high columns (diagonally braced) consisted of 3 large spherical mufflers, 4 tripping resistors, 2 capacitors, 2 extinguishing chambers | completely destroyed, diagonal and vertical insulators failed, breaker heads fell | 0
Cogenel | air blast | flexible conductors, dynamic analysis 0.5 g PGA design specification | mounted on steel A-frame w/ horizontal pressure vessel, breaker head mounted on 30 ft high columns (diagonally braced) consisted of 3 large spherical mufflers, 4 tripping resistors, 2 capacitors, 2 extinguishing chambers | completely destroyed, diagonal and vertical insulators failed, breaker heads fell | 0
Westinghouse | puffer | flexible conductors, dynamic analysis 0.5 g PGA design specification | no horizontal pressure vessel, no mufflers in breaker head | 0 | 0
GE | ATB4-6 SF6 | 0 | supported on steel frame | 2 column insulators broken , tank damage and corona ring broken | replaced
GE | ATB4-6 SF6 | 0 | supported on steel frame | 2 column insulators shattered | 0
Trench Electric & GE | 0 | 0 | 0 | 0 | 0
Trench Electric & GE | 0 | 0 | 0 | 0 | 0
Alsthom | 0 | 0 | 0 | 0 | 0
Alsthom | 0 | 0 | 0 | B & C broken , failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side | 0
Alsthom | 0 | 0 | 0 | A in half, B&C broken at flange, failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side | 0
Alsthom | 0 | 0 | 0 | failure occurred just below steel fitting at mid-height, broken conductor on circuit breaker side | 0
Porter & Brown Boveri | 0 | 0 | 0 | Brown Boveri failed on jaw side at base of insulators, Porter failed on hinge side in the porcelain | 0
Siemens-Allis | AVB4 | 0 | 0 | 0 | 0
Porter & Brown Boveri | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Supported on steel frame | destroyed, A phase broke at mounting flange for insulators | 0
0 | 0 | 0 | Supported on steel frame | damaged, C phase out of adjustment would not open | 0
0 | 0 | 0 | Supported on steel frame | A phase damaged, conductors from bus disconnects to bus stiffening insulators broke at base | 0
Brown Boveri | line side of CB 6032, single blade | 0 | Supported on steel frame | destroyed, broke at disconect flange all three phases | 0
0 | 0 | 0 | Supported on steel frame | 0 | 0
0 | 0 | 0 | 0 | destroyed, all three phases broke at base | 0
0 | 0 | 0 | 0 | 0 | 0
GE | ALUGARD 9L11LBA1B | 0 | 0 | destroyed, A & B phase broke at base | 0
0 | 0 | 0 | 0 | destroyed, A & B phase broke at base | 0
0 | 0 | 0 | 0 | destroyed, all three phases broke at base | 0
Ohio Brass | MPR Series F | 0 | 0 | 0 | 0
Ohio Brass | MPR Series F | 0 | 0 | destroyed, all broken at base of porcelain, may have been caused by swinging of wave traps which they were attached to by conductors | 0
GE | CD31023 SINGC | 0 | 0 | destroyed, broke at base of bushing | 0
GE | CD3123 SINGC | 0 | 0 | destroyed, broke at base of bushing | 0
GE Pot Dev CC | 4CD52A505C6C | 0 | 0 | destroyed | 0
0 | 0 | W. Pot. Dev Type FCA | 0 | destroyed | 0
0 | three phase | 0 | 0 | leaking oil around seals on bushings at the top of transformers, L-shaped connectors stressed beyond elestic limit at base causing transformers to walk and rock | 0
Allis-Chalmers | single phase | 0 | 500 kv bushing W Type O EBM 1675, concrete pad, anchored by steel gusset plates connected to concrete by 1" bolts and hooked over base flange | leaking oil around seals on bushings at the top of transformers, 1" bolts sheared at base causing transformers to walk (8" to 10") and rock | 0
Westinghouse | single phase | 0 | 500 kv bushing W Type O EBM 1675, concrete pad, anchored by embeded steel gusset plates hooked over base flange | leaking oil around seals on bushings at the top of transformers, L-shaped connectors stressed beyond elastic limit at base causing transformers to walk and rock | 0
GE | 0 | 0 | 0 | 0 | 0
GE | 0 | 0 | 0 | 0 | 0
Siemens-Allis | single blade | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | 0 | 0
Siemens-Allis | single blade | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assembly broke off at base on A phase | 0
Siemens-Allis | single blade | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assemblies fell to ground on all three phases | 0
Siemens-Allis | single blade | resistor assembly at top of jaw end of switch | switch supported on 6 pipe columns supporting frame that held all 3 phases of switch | Resistor assembly broke off at base on A phase | 0
0 | 0 | 0 | on top of A-frame racks supporting rigid jumper bus tie | 2 insulators failed at base dropping rigid bus and twisting flexible conductors. | 0
0 | 0 | bus suspension insulators | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | supported bus conductors | 0 | may have been caused by slack bus conductor strung from post to post | 0
GE | OA-MS | 0 | concrete pad, anchored by embeded steel gusset plates hooked over base flange | 0 | 0
GE | OA-MS | 0 | concrete pad, anchored by embeded steel gusset plates hooked over base flange | three types of failure, 1) rocking, 2) excessive movements of reactor bushings causing oil leaks, 3) terminal connector at top of bushing pulled off | 0
0 | Oil | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | three phase | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | oil | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | three phase | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | Oil | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | How is it installed | porcelain failed. | 0
0 | 0 | 0 | How is it installed | porcelain failed. | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 3 phase | 0 | 0 | 0 | 0
0 | 0 | Synchronous Condenser | 0 | misalignment causing loss of bearing pressure | 0
0 | 0 | Synchronous Condenser | 0 | misalignment causing loss of bearing pressure. Some could continue to run. | one replace bearing and others realign.
0 | SF-6 | 0 | 0 | 0 | 0
0 | Oil | 0 | 0 | 0 | 0
General Electric | ATB | Model not shown in data. | 0 | 0 | 0
General Electric | ATB | Model not shown in data. | 0 | leaking support column gaskets | N restored Feb 13, S restored Feb 26
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | 0 | Synchronous Condensers | 0 | loss of pressure, misaligned and bearing damage | realign bearings
0 | 0 | Synchronous Condensers | 0 | 0 | 0
0 | 0 | synchronous condenser | 0 | loss of oil pressure | 0
0 | 0 | synchronous condenser | 0 | 0 | 0
0 | 0 | 0 | 0 | 6 damaged bushings at Solemint and 3 flash overs at Saugus | 0
0 | 0 | 0 | 0 | Disconnect switches missaligned at Citrus SS and porcelain damage at Newhall | 0
0 | 0 | 0 | 0 | Several transmission towers on several lines had to have footings or foundations compacted. While some were under construction, most were existing in-service towers. There was no disruption from these failures. | 0
0 | 0 | 0 | use of tripod support | post insulator failed at base. In falling it pulled the bayonet and corona ring wich burned the operating rod. This is refered to as secondary damage. | Control rod and 3 post insulators were replaced.
Cole | 0 | 0 | 0 | Broken post insulator on line side. Unit opened and reclosed with bayonet on top of the bell on the female half of disconnect. | Replace insulator.
0 | 0 | 0 | 0 | Broken post insulator on line side. Reported as secondary damage. Need to review station for assessment. | Replace insulator.
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | From picture, the LA appears to be on line between OCB and DS, an unusal situation. | porcelain failed at base | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | Shifted on transfer car and slipped its rail chocks about 6 inches | 0
0 | 0 | 0 | 0 | 66 kV bushing cracked, fell over and cracked bowl on its top. | 0
0 | 0 | 0 | 0 | Four units sheared anchor bolts on one side and shifted 1 to 2 inches | 0
0 | 0 | 0 | 0 | support insulator broke. Rack pulled towards bus about 4" and three bus side bushings on 16 kV capacitor PCB flashed over and were replaced. | 0
0 | 0 | Transfer bus on 2A Bank | 0 | Fitting on transfer bus support failed allowing one end of bus to fall. Porcelain did not fail. | 0
GE | ATB | 0 | 0 | 0 | 0
GE | ATB | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | remained on supports with damage to oil seals, terminal taps and base connections | 0
0 | 0 | 0 | 0 | broke from steel post support pedestal and fell to ground | 0
GE | ATB | 0 | 0 | 0 | 0
0 | SF6 | 0 | 0 | 0 | 0
Westinghouse | SF6 non-seismic | 0 | 0 | 0 | 0
Westinghouse | SF6 non-seismic | Vincent is not on data sheets | 0 | Individual data is not vailable. 3 porcelain columns failed, 2 columns cracked of the 9 columns, 10 of 18 porcelain guys failed. 5 of 9 twisted clockwise as view from above. | 41 days before spares could be obtained.
Westinghouse | SF6 non-seismic | Vincent is not on data sheets | 0 | 4 porcelain guys on N and 7 guys on S failed. | Guy damage would not effect operation. Units were repaired and put back into service within 48 hrs.
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Vincent is not on data sheets. What is type? | How is it installed? | Post insulator failed. Unit out of alignment. | 0
0 | 0 | Probably don't have all DS1 | How is it installed? | 0 | 0
0 | 0 | Vincent is not on data sheets | How is it installed? | porcelain failed. | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Vincent is not on data sheets | How is it installed? | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Vincent is not on data sheets | 0 | Radiator leak. | restoration?
0 | 0 | Vincent is not on data sheets | 0 | LA damaged radiator fan. | 0
0 | 0 | Bus support | How is it installed? | 2 post insulators failed. How many did not fail? | 0
0 | 0 | Bus support | How is it installed? | 2 post insulators failed. How many did not fail? | 0
0 | Oil | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
General Electric | 8275998 | Single phase 220/66 kV TR. | 0 | 220 bushing gasket leaks. Anchorage was distressed. | Replace 220 kV bushing on 220/66 kV B phase TR.
General Electric | 8276000, -1, -2 | Single phase 220/66 kV TRs. | 0 | 0 | 0
General Electric | 8275997, -9 | Single phase 220/66 kV TRs. | 0 | 0 | 0
Westinghouse | 3418517, -8, -9 | Single phase 220/66 kV TRs. | 0 | 220 bushing gasket leaks. Anchorage was distressed. | Replace each 220 kV bushing on each single phase 220/66 kV TR.
Westinghouse | 3772575, 4088092,-3 | Single phase 220/66 kV TRs. | 0 | 220 bushing gasket leaks. Anchorage was distressed. | Replace each 220 kV bushing on each single phase 220/66 kV TR.
General Electric | ATB7 | 0 | 0 | One of the outside interrupter head bushing blew. From slack that was available it appears that head moved about 12". | 0
General Electric | ATB7 | 0 | 0 | Crack at sandring allowed SF6 to leak out. | Lower porcelain member had to be replaced.
General Electric | ATB7 | 0 | 0 | Porcelain interrupter head support columns failed. | Dead tank replacement unit used.
General Electric | ATB7 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
General Electric | ATB7 | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | Only one of the gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Interrupter head support column failed (column w/o CT) | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 (isolated) | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. Unit mounted on 3/4" elastomer pad | Only one gaskets on the 2 interrupter head bushings that were connected to each other blew. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 (isolated) | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. Unit mounted on sock isolators of | 0 | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 | These units were put in at a time when seismic awareness was low and only standard CBs were available. The interrupter heads on this unit weighed 3600 pounds vs 2600 for most other units. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 | These units were put in at a time when seismic awareness was low and only standard CBs were available. | Support structures were designed for 0.5g and were very beefy with welded tubular steel members. Each of 4 legs was bolted to slab with 4 bolts. There were no indications of distress in the structure or its anchorage. | The gaskets on the 2 interrupter head bushings that were connected to each other blew. Porcelain part of high pressure air supply broke. Support column containing CT failed. | Units were removed to pump plant for restoration. Spare parts were a difficulty with estimated delivery times of about 1 month with no guarantee. There was some cannibalization for parts.
General Electric | ATB7 | Same as for damaged units | Same as for damaged units | 0 | 0
0 | low design | 0 | 0 | 0 | 0
0 | low design | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | three phase | 0 | Well anchored | Minor oil leak at top connection of radiator to tank. | 0
0 | three phase | 0 | Well anchored | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
General Electric | ATB4 | 0 | 0 | CT leak on C phase | Completed 10/2.87 @ 0339
General Electric? | ATB4? | 0 | middle phase | Leaking nin-CT column | Completed 10/5/87 @ 1200. Note that it was after aftershock.
General Electric | ATB 4-6 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase, unit | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | nitrogen leak due to ruptured diaphram. | Completed 10/2/87 @ 0607.
0 | three phase, unit | 0 | 0 | 0 | 0
Westinghouse and ITE | 2300SF15000/20000-25 | 0 | 0 | 0 | 0
Westinghouse | 2300SF15000/20000-30 | 0 | 0 | not known | to be replaced
Allis Chalmers | oil | 0 | 0 | 0 | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | functional immediately after eq, EPRI report indicates all had leaking seals | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | porcelain column shattered | to be rebuilt
0 | 0 | frame mounted | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 3 o spare | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | 0 | 0
Allis Chalmers | 1-0140-24784-1,-3;2-0102-9162-3, 7 | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | 0 | 0
General Electric | 3o D572975 | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | 0 | 0
Pennsylvania | 3o 01823-5-1 | rail mounted, steel strap welded to TR and bolted to concrete base mat | 0 | Leaking 230 kV bushings. 2 or 3 bushings | Replaced "O" rings. Restored 11/2/87 @ 1630
General Electric | ATB5 230-20000-5-20 | 0 | 0 | Leak in non-CT column | Completed 10/3/87 @ 0227
General Electric | ATB5 230-20000-5-20 | 0 | 0 | Leak in non-CT column | Completed 10/4/87 @ 1654
General Electric | ATB4 | Written summary list ATB4 but data sheet gives W +M | 0 | 1 CT column | Completed 10/6/87 @ 2100. Note that repair was done after aftershock.
General Electric | ATB5 230-20000-5-20 | 0 | 0 | Leaks in CT columns | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | Leaks in CT columns | Completed 10/3/87 @ 0227
General Electric | ATB4 | 0 | 0 | 0 | 0
General Electric | ATB4 230-20000-6Y20 | Written summary list ATB4 but data sheet suggests ATB6 | 0 | Leak in 2 non-CT column and 3 CT columns | Completed 10/6/87 @ 2100. Note that repair was done after aftershock.
General Electric | ATB4 230-20000-6Y20 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
General Electric | three phase | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | oil | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | 0 | What type of equipment | 0 | Topping up needed but no leak found suggests that there was a leak that was self healing | 0
General Electric | ATB7 | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | oil | 0 | 0 | 0 | 0
General Electric | ATB 4-6 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | three phase | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | 0 | Are there 66 kV SF6 CBs? | 0 | Ruptured releif valve | 0
General Electric | ATB7 | 0 | 0 | non-CT columns leaking. crcked insulator. | 17 week lead time.
General Electric | ATB7 | 0 | 0 | 2 non-CT columns leaking. | complete 10/2/87 @ 2327
General Electric | ATB7 | 0 | 0 | 2 non-CT columns leaking. | complete 10/2/87 @ 1601
General Electric | ATB7 | 0 | 0 | There may be others that are not damaged. | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | oil | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | three phase | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | Topping up needed but no leak found suggests that there was a leak that was self healing | 0
0 | SF-6 | 0 | 0 | 0 | 0
General Electric | ATB 4-6 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Not sure of voltage | 0 | 0 | 0
0 | 0 | Not sure of voltages | 0 | Chipped bushing | 0
0 | three phase | 0 | 0 | 0 | 0
General Electric | ATB4 230-20000-0-20? | Note model no. indicated as Westinghouse. | 0 | 2 interrupter head bushings leaking, 1 CT and 1 non 0CT columns leaking. | repairs 60% complete 10/5/87. Note that repairs were not colpleted until after the aftershock.
0 | SF6 | 0 | 0 | 0 | 0
0 | oil | 0 | 0 | 0 | 0
General Electric | ATB4 230-20000-0-20? | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase | 0 | 0 | 0 | 0
0 | three phase | 0 | 0 | 0 | 0
0 | 0 | What type of CB? | 0 | Cracked 66 kV bushing. | 0
Westinghouse | 2300SF15000/20000-25 | 0 | 0 | 0 | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | leaking support column gasket. How many phases out? | Three days 14 hrs to repair
General Electric | ATB5 230-20000-5-20 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive.
General Electric | ATB5 230-20000-5-20 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive.
General Electric | ATB5 230-20000-5-20 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive.
General Electric | ATB5 230-20000-5-20 | 0 | 0 | functional immediately after earthquake, EPRI report indicates that all CBs eventually developed leaks | 0
General Electric | ATB5 230-20000-5-20 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive. Restored 10/4/87 @ 0330
General Electric | ATB5 230-20000-5-20 | 0 | 0 | leaking support column gasket. How many phases out? | Can be restored by 10/10 (9 days) working 24 hr shift if part arrive.
General Electric | ATB5 230-20000-5-20 | 0 | 0 | leaking support column gasket. How many phases out? | Three days 10 hrs to repair.
0 | 0 | 0 | frame mounted | 0 | 0
0 | 0 | 0 | How was it installed? | Failed porcelain column | Can be restored by 10/10 (9 days) working 24 hr shift if part arrives.
0 | 0 | 0 | 0 | 0 | 0
General Electric | 3o D582895, D596229 | 0 | Welded to embedded steel on mats | 0 | 0
0 | 0 | 0 | How is it mounted? | 0 | 0
0 | 0 | 0 | 0 | 4 post insulators for bus supports damaged. | Replaced 10/3/87 @ 2010
Allis Chalmers | oil | 0 | 0 | 0 | 0
0 | 0 | 0 | frame mounted | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
Allis Chalmers | single phase | 0 | anchored by gussets welded to embedded steel | 0 | 0
Westinghouse | 220000-072000 5066610 | 0 | anchored by gussets welded to embedded steel | 0 | 0
Westinghouse | 220000-072000 506668, -9 | 0 | anchored by gussets welded to embedded steel | functional, oil leaks at radiator flange. | 0
Westinghouse | 220000-072000 5069946, -7, -8 | 0 | anchored by gussets welded to embedded steel | functional, oil leaks at radiator flange. | 0
0 | 0 | 0 | How is it mounted? | Failure of porcelain. What voltage. What is significance of "Painted Bushing Cap"? | 0
0 | 0 | 0 | How is it mounted? | . What voltage. What is significance of "Painted Bushing Cap"? | 0
0 | 0 | 0 | 0 | Fitting on transfer bus broke?, What voltage? | 0
0 | 0 | What type of TR? | 0 | Leaking 66 kV bushing. | 0
Need manufacturer | 0 | 0 | 0 | Leaking bushings | Can be restored by 10/3 23:55 (2 Days 16 hrs). 1200 amp bushing was used instead of 1600 amp bushing as spare was not available.
oil | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | How were LA installed? | 0 | 0
0 | three phase | What type of TR: Radiator size and mounting, LA mounting, No. of Phases? | 0 | What was damage to bushings? | There was not disruption of service due to bushing damage. Was it repaired?
0 | three phase | 0 | 0 | 0 | 0
0 | 0 | The boom was moderate length and had small gussets to stiffen the boom-TR connection. | Installed on three porcelain standoffs. There was almost no slack between bushing and LA and between LA and bus support column. | Cracked at base. Hinge is consistent with pull on bus. | 0
0 | 0 | The boom was moderate length and had small gussets to stiffen the boom-TR connection. | Installed on three porcelain standoffs. There was almost no slack between bushing and LA and between LA and bus support column. | 0 | 0
Hitachi | 0 | 3-phase, Bushings mounted on top of tall cylinders. | 0 | Three of the six bushings leaked, were leaking and had to be removed to restore. One bushing had a hairline crack along its length. These are draw-type bushings and the cracked unit had a tight fit to the draw mechanism. | The three bushings that had shifted and were leaking were repaired in the bushing shop.
Westinghouse | 0 | 3 phase | 0 | The TR case, about 3-1/2' above base had a crack in a weld at a corner. | Using a center punch, metal was moved to close the crack.
Westinghouse | 0 | 3 phase | 0 | 0 | 0
0 | 0 | 3 phase | 0 | 0 | 0
General Electric | ATB7 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0
0 | SF-6 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0
0 | SF-6 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0
General Electric | ATB 4-6 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0
General Electric | ATB 4-6 | See TCLEE Mongraph 8, some equipment missing from drawings | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | only required adjustment | 0
0 | 0 | 0 | 0 | visibly damaged | 0
0 | 0 | 0 | 0 | seriously damaged | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
Mitsubishi | SF6 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 0 | 0
Mitsubishi | SF6 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 2 columns failed at base, Damage caused by interaction from adjacent equipment, pull over by WT | 0
0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 1 column failed at base, Damage caused by interaction from adjacent equipment, pulled over by WT | 0
0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 2 columns failed at base, Damage caused by interaction from adjacent equipment, pulled over by WT | 0
0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | both tripods failed | 0
0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 1 tripod failed | 0
0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 1 tripod failed | 0
0 | 0 | Qualified by a 0.5g 10 cycle sine-beat shake table test | 0 | 0 | 0
0 | 0 | Dynamic Analysis | Tripod Support, Center Break, picture page 32 ASCE reference | 0 | 0
Southern States | 0 | Center break, sine beat tested | heavily braced support | 1 column failed, see page 56 ASCE | 0
0 | 0 | Center break | 0 | 1 column failed, see page 56 ASCE | 0
0 | 0 | Center break | 0 | 0 | 0
0 | 0 | Center break | 0 | 1 column failed, see page 56 ASCE | 0
0 | 0 | Center break | 0 | 0 | 0
0 | 0 | Center break | 0 | 0 | 0
0 | 0 | Center break | 0 | 1 column failed, see page 57 ASCE | 0
0 | 0 | Center break | 0 | 0 | 0
0 | 0 | Center break | 0 | 2 column failed, see page 59 ASCE | 0
0 | 0 | Center break | 0 | 1 column failed, see page 59 ASCE | 0
0 | 0 | Center break | 0 | 1 column failed, see page 59 ASCE | 0
0 | 0 | Center break | 0 | 2 column failed, see page 59 ASCE | 0
Southern States | 0 | Center break, sine beat tested | heavily braced support | See page 56 ASCE | 0
0 | 0 | Center break | 0 | 0 | 0
0 | 0 | 0 | 0 | direct communication from Rulon Fronk | 0
0 | 0 | 0 | Post Supported | Failure in porcelain | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Post supported | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | direct communication from Rulon Fronk | 0
0 | 0 | 0 | 0 | direct communication from Rulon Fronk | 0
0 | 1 phase | 0 | 0 | direct communication from Rulon Fronk | 0
0 | 1 phase | 0 | 0 | direct communication from Rulon Fronk | 0
0 | 0 | 0 | 0 | failure of 1 post insulator restraint, see page 56 ASCE | 0
0 | 0 | 0 | 0 | failure of post insulator restraints, see page 57 ASCE | 0
0 | 0 | 0 | 0 | failure of post insulator restraints, see page 57 ASCE | 0
0 | 0 | 0 | 0 | Failure of support post insulators | 0
0 | 0 | Post restraint | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Cable restraint | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | Post insulators failed, base bolts stretched | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | Post insulator failed | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | Post insulators failed | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | Failed at based of column | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 3 phase | 0 | Lost LAs | 0
0 | 0 | 3 phase | 0 | 0 | 0
0 | 0 | single phase | 0 | 0 | 0
0 | 0 | single phase | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | All wave traps undamaged but restraint on one WT damaged | 0
0 | 0 | 0 | 0 | Post failed | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Most units are anchored with bolts through skid frame. | Some units showed signs of distress in the anchore bolts, that is, chipped paint or bent bolts. | 0
0 | 0 | Total number of CCVTs disagrees with number in TCLEE report page 61 | Note that these units are supported on a beam spanning 2 DS rather than on its own support sturcture. | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | 0 | Both support columns failed. | 0
0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | Note that a rigid bus connects the Bus 1 and Bus 2 Positions. | All of these failures were to the column that is connected by rigid bus to the adjacent switch. Note that these switches are braced in the direction of the rigid bus connection. | 0
0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. |  | Both support columns failed | 0
0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | 0 | unknown failure mode | 0
0 | 0 | Center break, Units supported on four columns with diagonal brace in plane of switch. Pict 10-3. Note that a rigid bus connects the Bus 1 and Bus 2 Positions in all positions except the bank positions, where most failures occurred. | 0 | Some of these units have been damaged, but their position is not known. | 0
0 | 0 | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | 2 LA failed at standoff | 0
0 | 0 | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | 1 failed at base of LA. | 0
0 | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All LA failed but it is not known if there are standoffs. | 0
0 | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All LA failed but it is not known if there are standoffs. | 0
0 | 0 | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | 0 | 0
0 | 3-phase | Schematic on page 66 of ASCE | LA bus connection to directly bushing. | All high voltage bushings moved. 2 LA failed at standoff, 1 at base of LA. | 0
0 | 3-phase | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | All high voltage bushings moved. Also leaks in low voltage bushings. All LA failed but it is not known if there are standoffs. Anchor bolts stretched. There was a oil leak but it is not known if it is just the bushings. | 0
0 | 3-phase | Schematic on page 66 of ASCE | LA bus connections not to bushings. | All high voltage bushings moved. 1 LA failed at standoff, 2 at base of LA. | 0
0 | 3-phase | Schematic on page 66 of ASCE | LA bus connection not directly to bushings. | It is not known if there are standoffs. | 0
0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS | Unit was tilting, but was functional. | 0
0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | Unit had to be removed and replaced, but damage not known. | 0
0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | Units tilted,but functional. | 0
0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS | 0 | 0
0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | 0 | 0
0 | 0 | 0 | Note that this unit had the post insulators supported on a beam spanning 2 DS rather than on its own support sturcture. | 0 | 0
0 | 0 | 0 | 0 | 2 at standoff , 4 at arrester | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 3-phase | 0 | 0 | 6 Leaking 230 kVbushings, 6 LA failed | 0
0 | 3-phase | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | There may be a slack problem in that there is a short flexible connection to a rigid bus that is supported by disconnect switch structures. Pot head support structure is also connected to the rigid bus. | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
ITE | Type DR-5 | 0 | 0 | These units had deformed operating mechanism that prevented their operation. None of the post insulators were damaged. | It took 2 days to identify the problem and the fix and 2 hour for each (3 phases) to make repairs after that.
ITE | Type DR-5 | 0 | 0 | These units had deformed operating mechanisms that prevented their operation. None of the post insulators were damaged. | It took 2 days to identify the problem and the fix and 2 hour for each (3 phases) to make repairs after that.
Cole | 0 | 0 | 0 | unknown damage | Post insulators used for bus supports in PE4,5,6 were canibalized to reconstruct DS.
Cole | 0 | 0 | rigid bus connection | One of the columns failed. 10 were adjacent to CB and were provided with good slack so that inertial loads were probably the cause of failure. One unit was connected to a bus with an intermediate drop and bus dynamics may have contributed to failure | Post insulators used for bus supports in PE4,5,6 were canibalized to reconstruct DS.
Cole | 0 | 0 | rigid bus connection | Both columns failed. Interaction between columns may have contributed to the dual failures. . | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | 1 column failed | 0
0 | 0 | 0 | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | both columns failed | 0
0 | 0 | 0 | Note that 12 units had flexible connections at ends of rigid bus connection adjacent DS | 0 | 0
0 | 0 | 0 | Standoffs failed | Standoffs failed | 0
0 | 0 | 0 | Unusual installation in that frame is much lower than that used for TRs. LA are on standoffs. There is marginal slack to a rigid bus that is supported on disconnect switches. | Standoffs failed | 0
0 | 0 | 0 | No Standoffs | Failed at base of LA | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | Unusual installation in that frame is much lower than that used for TRs. LA are on standoffs. There is marginal slack to a rigid bus that is supported on disconnect switches. | 0 | 0
0 | 0 | TR in accountic enclosure. Separately supported radiators. Conservator tank with 2 supports. LA supported on frame with standoffs. | Ao and Co LA drops from bus, Bo from bushing. see page 71 ASCE | Bo Bushing has damaged bus stud. All LA failed, A & C at standoffs and B at LA base. Conservator stretched bolts and shifted in slotted connections, strain piping and lost all 1000g oil. | 0
0 | 0 | TR in accountic enclosure. Separately supported radiators. Conservator on 2 supports above TR. LA supported on frame. . | All LA have bus drops from bus. | All failed at standoffs and were not damaged. Signs of oil leak (spray on conservator) but source could not be found. | 0
0 | 0 | TR in accountic enclosure. Separately supported radiators, which were moderately large. Conservator on top of radiators. LA supported on independent posts without standoffs. | LA drops from bus. | Signs of oil leak at valve inside of enclosure, but it looks old. | 0
0 | 0 | LA on boom without standoffs. High voltage LA have drops from bus. see page 71 ASCE | Unit anchored with gusseted angle to pull tabs. | 230 KV LA failed. They were boom mounted without standoffs. Small radiators. Flexible end anchors to pull tabs contributed to failure of bolted angles along side. | 0
0 | 0 | 0 | These units have marginal slack. | 1 WT w/ failed posts at lower sand ring, 2 failed welds at top of posts connecting to wave trap support channel. | Two units were restored by bolting angles between channel and post cap.
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | three phase | 0 | 0 | radiator leak | 0
0 | three phase | 0 | 0 | 0 | 0
Westinghous-Mitsubishi Power Breaker | 200-SFMT-63B | 0 | Has very good slack to DSs. Pict 1-35 | E91 A had a loose bolt at south east corner. | 0
Siemens-Allis & ITE | 0 | 0 | 0 | 0 | 0
GE | 4CD3 | Installed on 6-3/4" diameter 8'-6" tall | Good slack in bus connection | A failed at lower sand ring and B did not look damaged on original trip. Unit was removed and porcelain was fractured 1/3 of the way up from base. Ao is would be inertial loads. Pict 3-34, 28-36 | 0
GE | 0 | 0 | Units are on pedestals 6-3/4" diameter and 8'-6" tall | This unit was found removed 3/15/94. Pict 28-34 | 0
GE | 4CD3... | Units are on pedestals 6-3/4" diameter and 8'-6" tall | Good slack in bus connection. Pict 2-15 | 0 | 0
GE | 4CD3... | Supported on 6-3/4" 8'-6" tall | Good slack in bus connection. Pict 24-8 | 0 | 0
0 | 0 | A is Nisson Denki, B & C are GE. Pict. 24-4 | A & C have Bellville washers, B does not? | 0 | 0
Haeffey | 0 | mounted on 12" diameter post that is 7' high. Can is sealed in unusual way. Support post has 8 large gussets at base and top. Pict. 1-30, 28, 26, 25, 28-23, 22, 21 | 0 | 0 | 0
Westinghouse | 0 | Units have bellville washers. Support column is 13" diameter and 7'-8" tall. pict 28-27 | 0 | 0 | 0
Trench | 0 | Support column is 13" diameter and 7'-8" tall all connected to a large metal base. Pict 28-34 | 0 | 0 | 0
Southern States | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. | 0 | Support shaft failed so that it looked like a fatigue failure. Similar failure at RS E. Orientation of fractures are not consistant with position of arm. 92CL Pict 1-29,28,27,26,25. 101BL Pict1-21,20. 101BB Pict1-18,17,16,15. 91AB Pict 1-14. 28-24. Bus | 0
Southern States | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. | 0 | Porcelain failure at base. Fracture surface (hinge) suggests that it failed due to a pull by the bus. There were two failures adjacent to line drop. Pict 1-24,23,22,12,11. 28-24. Bus drop 1-34 indicated that swing at top of drop may have lifted drop. | 0
Cole | 0 | Units supported on two columns | 0 | All failed at the base of the porcelain. Only one column failed. column E82CLB, E82ALB, E83Ab1b1, E83Ab2b1, E81CLL, E72BLL, E7Cb2b2, E73Bb2b2, E73Ab2b1, E71CBL, E71ALB, Bank F 230 Bank, Bank F 230 Bbank, Bank F 220 BB, Pict 1-8, 1-7,2-37, 2-18 | 0
Cole | 0 | Units supported on two columns | 0 | Post insulators failed at sand ring. Both insulators failed. Pict 1-8 | 0
Cole | 0 | Units supported on two columns. Pict 28-32, 31 | 0 | Post insulators failed at sand ring. | 0
Southern States | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. Pict 1-36 | 0 | 0 | 0
Southern States | 0 | Support structure has heavy bracing in longitudinal and transverse directions. Units sine beat tested for 10 cycles at .5 g. | 0 | 0 | 0
Cole | 0 | Units supported on two columns. 8-1/2" x 5" with about 3/8" wall with long direction in line with closed arm. Pict 28-31 | 0 | 0 | 0
0 | 0 | Pict 28-32, 2-13 | on porcelain standoffs, Support plates look thin. | 0 | 0
0 | 0 | Support post is 6-3/4"diameter and 7'-10" high. Pict 3-38, 37,36,35,,33,32. | Units had Bellville washers. The base has small gussets. | Units all failed at the sand ring at base, except 230 Bus 2 A where damage was not obvious, but must have been it cracked. It did not have oil spill below it. Note that bus 2 side anchore bolts were streched and one was loose. On Bus 1 A & C o had st | 0
Westinghouse | 0 | Support columns is very large with gussets at top but not at base. Support column is 15" Square and 7'-4" tall from top of lower support to bottom of top support. Pict. 1-37,15 | Units did not have Bellville washers. | 0 | 0
0 | 0 | These units have much smaller section support column that 220 KV bus. Support post is 6-3/4"diameter and 7'-10" high. | Units had Bellville washers | Note that bus 2 side anchore bolts were streched and one was loose. On Bus 1 A & C o had streched bolts but were undamaged. Phase B did not strech but failed. Phase C gussett at base showed signs of distress. Pict 3-33 | 0
Westinghouse | 0 | 3 phase Auto transformer 220 to 230 KV | Radiators braced at the bottom | Weld to embedment failed. It was a poor weld and not much material was put down. The concrete was fractured where the embedment tried to pull out. The transformer moved about 14" to the north. Pict 2-10,, 9, 8, 7, 6, 28-32 | 0
Westinghouse | 0 | 3 phase Pict 2-13 | Radiators braced at the bottom, welded to embedment | 0 | 0
0 | 0 | 0 | 0 | Weld on one side channel failed. Other channel tore. Pict 2-35, 34, 33, 32, 29, 2-17 | 0
0 | 0 | Pict 24-6 | 0 | bolts failed on restraint, WT ok | 0
0 | 0 | Pict 24-7, 8 | 0 | 0 | 0
0 | 0 | Units supported on three columns. Pict 24-4 | 0 | 0 | 0
0 | 0 | Pict 28-29 | 0 | 0 | 0
General Electric | ATB | 0 | 0 | 0 | 0
General Electric | ATB | 0 | 0 | 0 | 0
Westinghouse | seismic | 0 | 0 | 0 | 0
Westinghouse | seismic | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
Siemans | 0 | 0 | 0 | 0 | 0
Westinghouse | Puffers | 0 | 0 | 0 | 0
0 | SF-6 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | broken | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | single phase | composite bushing | 0 | radiator leaks | 0
0 | single phase | composite bushing | 0 | 0 | 0
0 | 0 | Suspended | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0